## Bill No.1 General Items
BILL NO.1 - General Items
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
1 | Contractual Requirements
1.1 | Provide Performance Bond as specified in the General Conditions |  | 1 | sum
1.2 | Provide for Insurance of the Works in accordance with General Conditions of Contract. |  | 1 | sum
1.3 | Provide for Insurance of Construction Plant; in accordance with General Conditions of Contract |  | 1 | sum
1.4 | Provide for Insurance against damage to Persons and Property; in accordance with General Conditions of Contract. |  | 1 | sum
1.5 | Provide for Public Liability and Employers Liability Insurance, in accordance with General Conditions of Contract. |  | 1 | sum
1.6 | Provide for compliance with all relevant Construction, Safety, Health and Welfare Regulations. |  | 1 | sum
2 | Specified Requirements |  | 1
2.1 | Allow for the establishment and removal of offices and office equipment for the sole use of the Supervisor and include for any reinstatement. |  | 1 | sum
2.2 | Allow for full Maintenance of offices and office equipment for the Supervisor to the end of the defects notification period. |  | 1 | sum
2.3 | Provide for establishment and removal of telephone, telephone answering machine, internet connection and fax machine for the Supervisor. |  | 1 | sum
2.4 | Provide and maintain surveying equipment for the Supervisor. Include for the provision of all assistance required to the Supervisor. |  | 1 | sum
2.5 | Provide for the establishment, maintenance and removal of offices, storage areas, yards, staff facilities and all necessary plant and equipment for the use of the Contractor and include for any reinstatement. |  | 1 | sum
2.6 | Provide for establishment, maintenance and subsequent removal of permanent all site sign boards as required to meet EC requirements. Rates shall include for all costs from contract commencement to final acceptance. |  | 1 | sum
2.7 | Allow for all design work and all associated working drawings for both temporary and permanent works |  | 1 | sum
2.8 | Provide for concrete test cubes as required during the works. Include for making cubes, storing, curing, transport to laboratory, testing and reporting. |  | 1 | sum
2.9 | Allow for all traffic management measures and for the provision of all measures for the protection of the public including “Survey temporary regulations of traffic " . |  | 1 | sum
2.10 | Allow for the complete setting out of all of the works in accordance with the drawings |  | 1 | sum
2.11 | Allow for all topographical survey work required before, during and following completion of the construction works |  | 1 | sum
2.12 | Allow sum for the provision of assistance, materials and labour to sub-contractors |  | 1 | sum
2.13 | Allow for co-ordinating the construction of the works with Plant Installation Requirements. |  | 1 | sum
2.14 | Provide for pre-construction and progress photographs, as required |  | 1 | sum
2.15 | Allow sum for undertaking all subsoil investigations and testing required by the Contractor to determine the nature of ground to be excavated and the depths and quantities of groundwater |  | 1 | sum
2.16 | Allow sum for water testing of all structures and pipelines, and include for the provision and disposal of all water and for the provision of all labour, materials and equipment |  | 1 | sum
2.17 | Allow for the provision of as-built drawings based on the project designers' drawings with the agreement of the designers |  | 1 | sum
2.18 | Allow sum for the inclusion of all constructed facilities and elements in the national cadastral survey |  | 1 | sum
2.19 | Allow for the provision of Operations and Maintenance manuals |  | 1 | sum
2.20 | Allow sum for commissioning and obtaining all certificates and approvals for all parts of the works from the relevant Serbian authorities where necessary and where not covered elsewhere in the Bill of Quantities |  | 1 | sum
2.21 | Allow sum for Vehicles for the Supervisor: • One 5-door 4WD (off-road), AC, central locking and ABS breaking, diesel to be delivered to the Chief Resident Engineer. • One 5-door, with four / five seats, AC, central locking and ABS braking, to be delivered to the site-office of the Engineer. |  | 1 | sum
Total carried to Grand Summary €

## Bill No.2 Technology Part
Bill No. 2 - EQUIPMENT AND BUILDING WORKS FOR TECHNOLOGICAL PART
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
A. | TECHNOLOGICAL PART
I. | PREPARATION AND DOZING OF POLYELECTROLYTE
1.1 | Device for preparation of polyelectrolyte For preparation of the polyelectrolyte solutions, a device with manual starting has been foreseen for continuous preparations of the solutions. The device consists of 3 chambers for preparation of the solution from polyelectrolyte which is in the form of powder. 0.05 - 0.5 % solution shall be prepared. From the storage, through a dosing device, polyelectrolyte is mixed with controlled quantity of water and fed to the chamber for preparation of the solution equipped wit mixer. Afterwards, polyelectrolyte solution is, through dispersion chamber with mixed, fed into the chamber for maturing and dozing of the polyelectrolyte solution. The tank is equipped with level gauge, due to possible overflow if water supply is not disconnected. | see Tehn.spec. 3.1. | 1 | pcs
The device of the following characteristics has been foreseen: • maximum polyelectrolyte dosage 0.2 mg/l • maximum capacity up to 1000 l/h • water pressure 3-5 bar • dimensions W 980 x H 1605 x L 2296 mm stalled power 2.6 kW • consists of 3 chambers (preparation, maturing and storage) • feed by motor, controlled heating of pipes and hopper for powdered polyelectrolyte • control panel with automatic control of entire system .
1.2 | Polyelectrolyte dozing pump serves for transport of made up solution to the site of dozing. Polyelectrolyte dozing pump with frequency regulator has been foreseen. | see Tehn.spec. 3.1. | 2 | pcs
The pump of the following characteristics has been foreseen: • pump delivery 50-1400 l/h • dimensions W 230 x H 242 x L 874 mm • installed power 0.75 kW • 1 (one) in operation and 1 (one) standby (1+1)
I | PREPARATION AND DOZING OF POLYELECTROLYTE - TOTAL | Sub-total carried to Summary A. |  |  |  | 0
II. | SYSTEM FOR PRODUCTION AND DOZING OF ClO2 FROM TWO-COMPONENT POWDER
| System for production and dozing of ClO2 from two-component powder represents production system of chlorine dioxide with purity of 99,9%. It is a question of non-explosive two-component product in the form of powder, intended for obtaining 0,3% solution for safe and disinfected water. After making up 0,3% solution, such solution should remain of high quality and be usable in the period of 30 to 40 days (depending on storage conditions). Necessary dosage of chlorine dioxide is 0,05 mg/l. | see Tehn.spec. 3.2.
2.1 | Ultrasonic flowmeter for DN 1200 - external mounting via pipe single channel |  | 1 | pcs
2.2 | Electromotor piston-diaphragm dozing pump version PP, Q = 60l/h, Pmax = 10 bar and inlet for external pulse, motor with integrated frequency regulator, P=0,50kW, complete with connection set: • basket strainer with filter • check valve | see Tehn.spec. 3.2. | 2 | pcs
2.3 | Tank PE V=5000 lit, cylindrical | see Tehn.spec. 3.2. | 2 | pcs
2.4 | Digital controller for chlorine dioxide, LCD display, outlet: two On/Off proportional points | see Tehn.spec. 3.2. | 1 | pcs
2.5 | Amperometric probe for chlorine dioxide, range 0-2 mg/l temperature compensated 5-50oC max 1 bar | see Tehn.spec. 3.2. | 1 | pcs
2.6 | Off-line probe casing | see Tehn.spec. 3.2. | 1 | pcs
2.7 | Electrical cabinet PVC 400x400x250 | see Tehn.spec. 3.2. | 1 | pcs
2.8 | Automatic dozing controller based on flow and residual | see Tehn.spec. 3.2. | 1 | pcs
II. | SYSTEM FOR PRODUCTION AND DOZING OF ClO2 FROM TWO-COMPONENT POWDER - TOTAL | Sub-total carried to Summary A. |  |  |  | 0
III. | STATION FOR RAW WATER NEUTRALIZATION
| STATION FOR RAW WATER NEUTRALIZATION Proposed CO2 injection point is in the room through which passes raw water pipeline, and which is close to dam, where CO2 would be injected directly into raw water pipeline Ø 900 mm. Adopted concentration of CO2 is 40 mg/l. |  |  |  |  | 0
Variable values in the process are inlet pH and water flow. Control of CO2 dozing process is proposed proportionally to the flow and according to desired pH. Measurement of raw water flow, as well as measurement of pH is installed in the plant. Dozing equipment will use signal of the existing devices for adjustment of the current CO2 flow. Control of dosing will be through local PLC. To change dosages of carbon dioxide in accordance with various needs, it is necessary to provide a dozing panel with control valve for continuous adjustment of CO2 flow.
It is necessary that the pressure of carbon dioxide is above the water pressure by a minimum of 1 bar which provides good gas dispersion into water. Time needed for complete dissolution of carbon dioxide is 10 to 15 seconds. It has been foreseen to install carbon dioxide monitoring in the room where the equipment for carbon dioxide injection is placed and to prepare safety procedure which shall prescribe measures to be taken in the event that leakage is noticed, and/or increased level of carbon dioxide.
3.1 | CO2 storage tank • tank with vacuum-perlite insulation, intended for storage of liquid oxygen, capacity 20m3; | see Tehn.spec. 3.2. | 1 | pcs
3.2 | Liquid carbon dioxide evaporator • liquid carbon dioxide evaporator with evaporation capacity of 180 kg/h, installed power 15 kW | see Tehn.spec. 3.2. | 1 | pcs
3.3 | Gaseous carbon dioxide pipeline • gaseous CO2 pipeline from the gasification station to the dozing panel, pipeline length ca. 30 m, dimension 3/4", material Č 4580 | see Tehn.spec. 3.2. | 1 | pcs
3.4 | Panel for carbon dioxide continuous dozing • line for pressure control with inlet valve, filter, main pressure controller • carbon dioxide flowmeter with pressure indicator • flow controller, bypass with manual control valve for manual control • terminal for power supply and transmission of signal to control valve • PLC for dozing control | see Tehn.spec. 3.2. | 1 | pcs
3.5 | Diffusers for injecting CO2 • injection porous diffuser in the form of candle - 4 pieces, mutually connected for supply of gaseous CO2 (check valves, globe valves) | see Tehn.spec. 3.2. | 1 | pcs
3.6 | Detection and warning of CO2 leakage | see Tehn.spec. 3.2. | 1 | sum
3.7 | Assembly of GS injection station equipment | see Tehn.spec. 3.2. | 1 | sum
III. | STATION FOR RAW WATER NEUTRALIZATION | Sub-total carried to Summary A. |  |  |  | 0
IV. | PRODUCTION AND DOZING OF SODIUM HYPOCHLORITE FROM SALT
4.1. | PLANT FOR PRODUCTION OF SODIUM HYPOCHLORITE FROM SALT FOR WATER DISINFECTION
From the pipeline water is transported to softener where calcium and magnesium ions are removed and softened water is obtained. Softened water is fed to electrolyzer by the dozing pump where it is mixed with dissolved sodium chlorite which is by other dozing pump fed from the tank with the concentrated solution of sodium chlorite. In the electrolyzer, which is supplied by direct current from energy part, chemical reaction occurs where fed in solution converts into hypochlorite and is fed to the tank afterwards. During the reaction of hypochlorit synthesis, hydrogen is developed which is discharged into atmosphere by ventilation system. By automatic devices, optimum production of hypochlorit is realized. Obtained hypochlorite solution is injected into the pipeline by diaphragm pumps. The analyzer receives information on chlorine concentration and through the pumps the set concentration is manatained. In this way, a continuous production of hypochlorite with automatic control of process, dozing and measurement of residual chlorine is realized.
Plant of the following characteristics has been foreseen: • equivalent chlorine capacity (Cl2) 4.0kg/h • flow of saturated solution 30% 40l/h • flow of softened water 360l/h • total flow of electrolyte 400l/h • salt consumption ~ 12kg/h • electrical energy consumption ~ 20kWh • power supply voltage 150-270V, 50Hz • outlet concentration of NaOCl 0.9-1.0% • plant dimensions (W x D x H) 2500 x 2750 x 2800 mm
4.1.1. | ELECTROLYZER capacity 1000 gr of equivalent Cl2/h
| Electrolyzer of the following characteristics has been foreseen: • equivalent Cl2 capacity 24kg/dan • inlet electrolyte 30 gr/l NaCl • conversion level (kgNaCl/1kgCl2) 2.8-3.0 • inlet water temperature 5-20°C • salt consumption 72 kg/day • optimum electricity consumption 5.0kWh | see Tehn.spec. 3.7. | 4 | pcs
4.1.2. | WATER SOFTENER
| Water softeners of the following characteristics are foreseen: • column volume 32l • mass volume 30 l • flow 100 l/h • operating temperature 4-35 °C • operating pressure 2.5-5 bar • regenerans is saturated solt solution • salt/reg consumption 6 kg • dimensions 180mm x 1850mm | see Tehn.spec. 3.7. | 4 | pcs
4.1.3. | SOFTENED WATER TANK
| Tank of the following characteristics has been foreseen:: • dimensions 220mm x 160mm x 355mm • capacity 7.5l • PEHD casing • overflow connections 1/2 " • level control by level detector | see Tehn.spec. 3.7. | 4 | pcs
4.1.4. | SALT SATURATOR
| Saturator of the following characteristics has been foreseen: • dimensions 900 x 2200 x 15mm • capacity 1400l • salt mass 1500kg • salt level indicator • level control by level detector | see Tehn.spec. 3.7. | 1 | pcs
4.1.5. | SODIUM HYPOCHLORITE TANK
| Tank of the following characteristics has been foreseen: • dimensions 800 x 2000 x 15mm • capacity 1000l • NaOCl volume 900l • material PEHD • level control by level detector (max/min) | see Tehn.spec. 3.7. | 1 | pcs
4.1.6. | DOZING PUMP FOR SATURATED SALT SOLUTION
| Pumps of the following characteristics have been foreseen: • diaphragm electromagnetic for aggressive • pump delivery 0-15 l/h • power 40W | see Tehn.spec. 3.7. | 4 | pcs
4.1.7. | DOZING PUMP FOR SOFTENED WATER
| Pumps of the following characteristics have been foreseen: • diaphragm electromagnetic • delivery 0-65 l/h • power 40W | see Tehn.spec. 3.7. | 8 | pcs
4.1.8. | POWER SUPPLY UNIT WITH RECTIFIER
| Power supply unit of the following characteristics has been foreseen: • supply 3 x 220/380 V • maximum power 6kWh • dimensions (W x D x H mm) 640 x 480 x 860mm | see Tehn.spec. 3.7. | 4 | pcs
4.1.9. | DISTRIBUTION CABINET SENSOR LEVEL
| Distribution cabinet of the following characteristics has been foreseen: • supply 220 • maximum power 40W | see Tehn.spec. 3.7. | 2 | pcs
4.1.10. | HYDROGEN DILUTION VENTILATION SYSTEM
| Fan of the following characteristics has been foreseen: • power 50W • maximum air flow 400 m3/h • maximum pressure 200 Pa • dimensions 212mm x 275mm | see Tehn.spec. 3.7. | 4 | pcs
4.1.11. | CONTROL PROCESS AUTOMATION PLC | see Tehn.spec. 3.7. | 4 | pcs
4.1.12. | CONTROL-MONITORING PC CONFIGURATION - monitoring, communications and control software | see Tehn.spec. 3.7. | 2 | pcs
4.1 | PLANT FOR SODIUM HYPOCHLORITE PRODUCTION FROM SALT FOR WATER DISINFECTION - TOTAL | Sub-total carried to Summary IV.
4.2. | AUTOMATIC DOZING SYSTEM ACCORDING TO FLOW
| System of the following characteristics has been foreseen: • capacity 0 – 60 l/h • maximum water flow that can be chlorinated 166 l/s • electrical energy consumption 150Wh | see Tehn.spec. 3.7. | 4 | pcs
4.2.1. | DOZING PUMP FOR AGGRESSIVE MEDIA
| Pumps of the following characteristics have been foreseen: • diaphragm electromagnetic for aggressive media • power 40W | see Tehn.spec. 3.7. | 4 | pcs
4.2.2. | STAB PROPELLER FLOWMETER
| Flowmeter of the following characteristics has been foreseen: • supported pipe diameter: DN15 – DN100 with short sensor DN100 – DN400 with long sensor | see Tehn.spec. 3.7. | 1 | pcs
4.2.3. | FLOW SENSOR FOR AGGRESSIVE MEDIA
| Sensor of the following characteristics has been foreseen: • intended for aggressive media • control: PLC pumps | see Tehn.spec. 3.7. | 4 | pcs
4.2.4. | ELECTROMAGNETIC VALVE FOR AGGRESSIVE MEDIA
| Valve of the following characteristics has been foreseen: • intended for aggressive media • control: PLC | see Tehn.spec. 3.7. | 1 | pcs
4.2.5. | CHECK VALVE FOR AGGRESSIVE MEDIA
| Valve of the following characteristics has been foreseen: • intended for aggressive media | see Tehn.spec. 3.7. | 4 | pcs
4.2.6. | DIFFUSER
| Diffuser of the following characteristics has been foreseen: • intended for aggressive media | see Tehn.spec. 3.7. | 1 | pcs
4.2.7. | ELECTRICAL CABINET OF AUTOMATIC DOZING SYSTEM
| Cabinet of the following characteristics has been foreseen: • power supply 220 V, 50 Hz • power 200W | see Tehn.spec. 3.7. | 1 | pcs
4.2.8. | CONTROL-MONITORING PC CONFIGURATION - monitoring, communications and control sofware | see Tehn.spec. 3.7. | 1 | pcs
4.2 | AUTOMATIC DOZING SYSTEM ACCORDING TO FLOW - TOTAL | Sub-total carried to Summary IV.
4.3. | AUTOMATIC DOZING SYSTEM ACCORDING TO RESIDUAL
| System of the following characteristics has been foreseen: • capacity 0 – 60 l/h • maximum water flow that can be chlorinated 166 l/s • electrical energy consumption 200w | see Tehn.spec. 3.7. | 4 | pcs
4.3.1. | DOZING PUMP FOR AGGRESSIVE MEDIA
| Pumps of the following characteristics have been foreseen: • diaphragm electromagnetic for aggressive media • power 40W | see Tehn.spec. 3.7. | 4 | pcs
4.3.2. | RESIDUAL CHLORINE ANALIZER
| Analyzer of the following characteristics has been foreseen: • measurement range of 0-500 mg/l • sensitivity 0-0.01 mg/l • alarms for maximum/minimum residual | see Tehn.spec. 3.7. | 1 | pcs
4.3.3. | FLOW SENSOR FOR DOZING PUMPS
| Sensor of the following characteristics has been foreseen: • intended for aggressive media • control: PLC pumps | see Tehn.spec. 3.7. | 4 | pcs
4.3.4. | ELECTROMAGNETIC VALVE FOR AGGRESSIVE MEDIA
| Valve of the following characteristics has been foreseen: • intended for aggressive media • control: PLC | see Tehn.spec. 3.7. | 1 | pcs
4.3.5. | CHECK VALVE FOR AGGRESSIVE MEDIA
| Valve of the following characteristics has been foreseen: • intended for aggressive media | see Tehn.spec. 3.7. | 4 | pcs
4.3.6. | DIFFUSER
| Diffuser of the following characteristics has been foreseen: • intended for aggressive media | see Tehn.spec. 3.7. | 2 | pcs
4.3.7. | ELECTRICAL CABINET OF AUTOMATIC DOZING SYSTEM
| Cabinet of the following characteristics has been foreseen: • power supply 220 V, 50 Hz • power 200W | see Tehn.spec. 3.7. | 1 | pcs
4.3.8. | CONTROL-MONITORING PC CONFIGURATION - monitoring, communications and control software | see Tehn.spec. 3.7. | 1 | pcs
4.3 | AUTOMATIC DOZING SYSTEM ACCORDING TO RESIDUAL - TOTAL | Sub-total carried to Summary IV.
IV. | SUMMARY IV. - PRODUCTION AND DOZING OF SODIUM HYPOCHLORITE FROM SALT
Amount (euro)
4.1. | PLANT FOR PRODUCTION OF SODIUM HYPOCHLORITE FROM SALT FOR WATER DISINFECTION
4.2. | AUTOMATIC DOZING SYSTEM ACCORDING TO FLOW
4.3. | AUTOMATIC DOZING SYSTEM ACCORDING TO RESIDUAL
IV | PRODUCTION AND DOZING OF SODIUM HYPOCHLORITE FROM SALT
IV. | PRODUCTION AND DOZING OF SODIUM HYPOCHLORITE FROM SALT | TOTAL carried to Summary A. |  |  |  | 0
A | SUMMARY A. - TECHNOLOGICAL EQUIPMENT
Amount (euro)
I | PREPARATION AND DOZING OF POLYELECTROLYTE
II | SYSTEM FOR PRODUCTION AND DOZING OF ClO2 FROM TWO-COMPONENT POWDER
III | STATION FOR RAW WATER NEUTRALIZATION
IV | PRODUCTION AND DOZING OF SODIUM HYPOCHLORITE FROM SALT
A. | TECHNOLOGICAL EQUIPMENT TOTAL | TOTAL carried to Summary Bill No. 2 |  |  |  | 0
B. | FACILITY FOR DOZING OF CHEMICALS - BUILDING WORKS
I | HOUSE AND WOODWORK PAINTING
5.1.1 | Stripping the old paint and painting of walls and ceiling by dispersive paints. All surfaces are to be stripped and washed from paint. Plish, fill with plastic putty minor damage and fill with emulsion putty. Paint with dispersive paint in two passes according to customer's choice. | see Tehn.spec. 6.1., 10. | 800 | m2
5.1.2 | Painting the existing metal windows, doors and radiators by metal paint, with prior stripping the old paint. Prior to painting, remove old paint and corrosion by chemical and physical means, polish and clean. Apply impregnation and primer on windows and afterwards pre-fill and grind. After applying the first layer of metal paint, fill and polish. Apply second coat of metal paint, in shade according to customer's choice. | see Tehn.spec. 6.1., 10. | 150 | m2
I | HOUSE AND WOODWORK PAINTING - TOTAL: | Sub-total carried to Summary B.
B. | FACILITY FOR DOZING OF CHEMICALS - BUILDING WORKS - TOTAL | TOTAL carried to Summary Bill No. 2
| SUMMARY Bill No. 2 |  |  |  |  | Amount (euro)
A. | TECHNOLOGICAL EQUIPMENT
B. | FACILITY FOR DOZING OF CHEMICALS - BUILDING WORKS
Bill No. 2 | EQUIPMENT AND BUILDING WORKS FOR TECHNOLOGICAL PART | Total carried to Grand Summary - PART 1

## Bill No.3 Ozone Block
Bill No. 3 - OZONE BLOCK
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
A. | MECHANICAL EQUIPMENT
I | OZONATION EQUIPMENT
a. | Ozonation system general data |  |  |  |  | 0
| Ozone system will include on-site cable and pipe connecting |  |  |  |  | 0
| Process data: |  |  |  |  | 0
| Max. flowrate, future extension 1000 l/s |  |  |  |  | 0
| Ozone dosage 1,5 mg/l |  |  |  |  | 0
| Maximum ozone dosage 3,0 mg/l |  |  |  |  | 0
| Number of ozonation lines 2 |  |  |  |  | 0
| Number of contact chambers 2 x 150 m³ |  |  |  |  | 0
| Number of reaction chambers 2 x 150 m³ |  |  |  |  | 0
| Water depth in chambers 4,85 m |  |  |  |  | 0
| Contact time 5 - 12 min |  |  |  |  | 0
| Ozone introduction system Diffusers |  |  |  |  | 0
Fluid for production liquid oxygen
b. | Ozone generator |  |  |  |  | 0
| Scope of supply |  |  |  |  | 0
| Equipment shall be produced according to DIN 19627 Standard, fully automatic, consisting of all necessary equipment for economically efficient ozone production based on principle of silent electrical discharge. Ozone production from technical oxygen, fully assembled unit with all necessary instrumentation, piping and cabling and standardized control cabinets made of steel, coated, mounted, including piping and cabling. |  |  |  |  | 0
| Ozone generator vertically mounted, as tubular heat exchanger, with closed loop cooling system, baffle plates for cooling water circulation, equipped with high voltage electrodes (316Ti, 316L), stress free dielectric with a maximum diameter of 11mm made of high quality heat-resistant borosilicate glass. grounded tubes of the heat exchanger, the dielectric and high voltage electrodes are centred relative to one another forming two parallel gaps where discharging takes place. Electrodes and dielectrics are made of durable borosilicate glass with minimum thickness of 1.2 mm so as to prevent dielectric failure. Replacement of electrodes is guaranteed for ten years free of charge, as necessary. High voltage electrodes directly connected to converter without fuses. Electrodes must not operate at more than 30% of rated breakdown voltage. Ozone generator equipment includes flowmeters for monitoring gas and cooling water flow, control devices for controlling cooling water temperature, as well as pressure control valves. |  |  |  |  | 0
| Every single ozone generator must be equipped and controlled with Programmable Logic Controller, type as Siemens S7 or similar. |  |  |  |  | 0
| Special power supply unit converting standard supply voltage to high voltage of medium frequency, with rectangular waveform signal. Power supply unit shall meet IP54 requirements. |  |  |  |  | 0
| Fully equipped with "ON/OFF" switches and emergency switches. Prepared for manual and automatic adjustment of ozone production by changing converter frequency. |  |  |  |  | 0
| Electrical equipment cabled, installed in cabinets, including equipment necessary for operation and automatic control of the unit: |  |  |  |  | 0
| · circuit breaker |  |  |  |  | 0
· main switch
· potential-free contacts for transmission of fault messages (incl. type as SPS- Siemens S 7 or similar)
| · automatic cabinet climate control system |  |  |  |  | 0
Ozone generator controls shall consist of:
· flow indicator
| · pressure indicator |  |  |  |  | 0
| · cooling water temperature indicator |  |  |  |  | 0
| · TP 170 operator panel showing operation mode, malfunctions and line charts of the system parameter changes. |  |  |  |  | 0
| Ozone generator of the following characteristics: |  |  |  |  | 0
· fluid for production oxygen
· design capacity 5,4 kgO3/h
· design ozone concentration
| (cooling water temperature +5°C) 179g/m3 |  |  |  |  | 0
| · design ozone concentration |  |  |  |  | 0
| (cooling water temperature +25°C) 148g/m3 |  |  |  |  | 0
| · gas operating pressure 1.2 bar |  |  |  |  | 0
| · outlet pressure 0.9 bar |  |  |  |  | 0
| · max. cooling water temperature 25°C |  |  |  |  | 0
| · needed cooling water pressure 1-2 bar |  |  |  |  | 0
| · power supply 400V/50 Hz/3Ph/N/PE |  |  |  |  | 0
| · nominal operating power 60 KWh/h |  |  |  |  | 0
1 | Ozone generator
| Mounted ozone generator, including power supply unit, with complete set of pipes and fittings for gas and cooling water | see Tehn.spec. 3.3., 8.3. | 2 | pcs |  | 0
2. | Diffusion system
Total number of lines 2
| Total number of chambers for introducing ozone 2 |  |  |  |  | 0
Total number of diffusers: 66 + 4 (standby)
| Diffusion system characteristics: |  |  |  |  | 0
| type: circular ceramic diffusers |  |  |  |  | 0
diameter 173mm
nominal gas flowrate 2.2 Nm3/h
maximum gas flowrate 3.0 Nm3/h
minimal gas flowrate 0.2 Nm3/h
Diffuser material ceramics / 316 Ti or equivalent
diffusion piping system 316 Ti or equivalent
| Complete system for introducing ozone for both chambers, as described above | see Tehn.spec. 3.3., 8.3. | 70 | pcs |  | 0
3. | Residual ozone destruction
For destruction of residual ozone, which will be entrained with devolatilized oxygen, installation of two residual ozone destruction units operating according to thermo-catalytic principle, one as operating and the other as standby has been foreseen. Each ozone destructor is capable of destroying maximum injected ozone/oxygen gas mixture at design concentration. The units will be constructed as cylindrical vessels made of 316 Ti or equivalent material, with integrated preheating zone and sufficient catalyst for residual ozone destruction, completely assembled and mounted including extraction fan, connection box and temperature control via solid state relays.
Residual ozone destruction unit of the following characteristics:
type catalytic with preheating
preheating electrical
gas flowrate up to 43 Nm3/h
control relay
installed power 0.27 KW
fan installed power 0.65 KW
max. conc. of ozone in outlet gas 0.1 ppm
On top of each chamber one demister made of 316 Ti is to be mounted to remove water droplets from off gas.
| Furthermore, a safety valve, which will prevent overpressure or vacuum in chambers, is to be installed. |  |  |  |  | 0
| Pipe connection systems for two destruction units, of which one is standby. |  |  |  |  | 0
| Complete residual ozone destruction unit as described above | see Tehn.spec. 3.3., 8.3. | 2 | pcs |  | 0
4. | Ozone ambient air monitor |  |  |  |  | 0
A continuous air monitor for continuous control of ozone concentration in air is to be installed, in accordance with Directive ZH 1/474. In case of exceeding set limit values,
· acoustic and optical alarm
| · stopping of ozone production |  |  |  |  | 0
| · switching on the emergency ventilation |  |  |  |  | 0
| Actual ozone concentration will be shown via 4 – 20 mA signal in supervision room or at display installed beside the door of the ozone equipment room. The sensors measuring principle is based on electrochemical cell. |  |  |  |  | 0
| Measuring medium ozone |  |  |  |  | 0
Detection range (standard) 0 – 3,00 ppm
| Humidity 0 – 99 % r.h. |  |  |  |  | 0
| Pressure 900 – 1100 hPa |  |  |  |  | 0
| Output signal 0,2 – 1 mA or 4 – 20 mA |  |  |  |  | 0
| Ambient temperature -15 - +45°C |  |  |  |  | 0
| Casing protection IP 54 |  |  |  |  | 0
| Complete ozone ambient monitor unit as described above |  | 2 | pcs |  | 0
5. | Emergency ventilation |  |  |  |  | 0
| Emergency ventilation for each room where ozone pollution is possible, with three air exchange in the room, with all necessary equipment, connections, cables, etc., in accordance with local regulations. |  |  |  |  | 0
| Complete emergency ventilation unit as described above. |  | 1 | pcs |  | 0
6. | Analyzer of ozone in outlet gas |  |  |  |  | 0
| Ozone generator will be equipped with a device for measuring ozone concentration in outlet gas. Continuous measuring by UV photometric method will be carried out. The quantity of ozone per m³ independently of the pressure and temperature of gas mixture, in accordance with VDI-Regulation 2468/6. |  |  |  |  | 0
| The device consists of highly reliable process photometer installed inside coated steel cabinet (IP 65, NEMA 4X). The system includes internal sampling pump with automatic purging and zero calibration. Digital LED display will show the actual ozone concentration in g/m³. |  |  |  |  | 0
| Measuring method UV-photometric |  |  |  |  | 0
UV lamp low pressure mercury lamp
Display 7-segment, LED, 4 digits
concentration range 0—300 g/nm³
concentration error +/- 0.5% max.
recommended flowrate 0.2 do 1 l/min
pressure drop approximately 3 mbar at 0.5 l/min
response time approximately 1s
deviation 0,2 % daily, after 10-minute heating
allowed pressure max. 2,5 bar
ambient temperature 0-50 C
concentration output signal 4 - 20 mA isolated)
concentration 0 - 10 V (isolated)
setting control inputs to zero (24 V, 6 mA, isolated)
lamp control outputs (relay contact, 30 V, 1 A)
| Ozone analyzer as described above | see Tehn.spec. 3.3 | 2 | pcs
7. | Analyzer of ozone in water
Analyzer of ozone concentration in water is to be installed in outlet
piping, so as to monitor ozone concentration in water fed to
distribution chamber. The system will be equipped with internal pump
with automatic purging and zero calibration. Actual concentration
(in g/m3) shall be readout on digital LED display:
Display 7-segment, LED, 4 digits
concentration range 0—300 g/nm³
concentration error +/- 0.5% max
recommended flowrate 0.2 do 1 l/min
pressure drop approximately 3 mbar at 0.5 l/min
response time approximately 1s
allowed pressure max. 2,5 bar
output signals 4 – 20 m, 0-10 V
Manufacturer: BMT or similar
Type: 964 C or similar
| Ozone analyzer as described above | see Tehn.spec. 3.3 | 2 | pcs
8. | Ozonation process monitoring and control system
Ozonation process monitoring and control system is provide via PLC-a
| PLC will provide automatic control of entire ozonation system including auxiliary systems. Therefore, interface terminals (connective or "intelligent") are to be provided within distribution cabinets. Manual control (in distribution cabinets), unless emergency controls are in question, will be via PLC. Emergency controls and protection will be wired with main contactors or circuit switches - signalling via PLC. | see Tehn.spec. 3.3 | 1 | pcs
9. | Pipe connections and instruments
Complete system of pipe connections and instruments, including P&ID, pipe connections include connecting ozone generator with chambers, including all necessary equipment, fittings and valves.
| Pipe connections and instruments, as described above | see Tehn.spec. 3.3 | 1 | set
10. | Compressor
Compressor supplying dry and clean air suitable for delivered instruments, including all necessary equipment, fittings, valves, connections, cables, etc.
| Compressor, as described above | see Tehn.spec. 3.3 | 1 | pcs
I. | OZONATION EQUIPMENT- TOTAL | Sub-total carried to Summary A.
II | LIQUID OXYGEN GASIFICATION STATION
1. | Supply, transport and assembly of vertical tank with thermal vacuum insulation for storage of oxygen for ozone production of diameter 2.5 m and height of around 6 m with steel legs (which is mounted on concrete slab) together with oxygen evaporator and other appertaining equipment (valves, pressure gages, etc.) necessary for normal tank functioning (transfer). A distribution cabinet is to be provided on the plateau with electric service for tank-vehicle transporting oxygen. | see Tehn.spec. 3.3
cylindrical type - vertical
tank volume 20 m3
| diameter x height ~ 2,5x6 m |  | 1 | pcs
2. | Concreting bed plate of reinforced concrete to place and assembly of oxygen tank, evaporator and electric cabinet.
| Bad plate dimensions shall be 6x5,5 m and thickness 0,4 m. |  | 13.2 | m3
3. | Supply and construction of wire fence with steel post gate at distance of 2m and height of 2 m. Gate 1,6x2 m |  | 21 | m
II | LIQUID OXYGEN GASIFICATION STATION - TOTAL | Sub-total carried to Summary A.
III | MECHANICAL EQUIPMENT
1. | Sluicegate with electric actuator
Sluicegate with electric actuator of stainless steel on concrete channel for outlet of ozonated water on sand filters
1.1 | 1400x2000 | see Tehn.spec. 3.3 | 2 | pcs
1.2 | 1000x1000 | see Tehn.spec. 3.3 | 2 | pcs
2. | Short body gate valve DN 150
Short body gate valve of stainless steel installed on piping for piping outflow and discharge
| DN 150 PN 10 | see Tehn.spec. 3.3., 8.5. | 2 | pcs
3. | Piping DN 150 of stainless steel | see Tehn.spec. 8.4. | 10 | m
4. | Cover of stainless steel DN 800 on ozonation chambers | see Tehn.spec. 8.4. | 4 | pcs
III | MECHANICAL EQUIPMENT - TOTAL | Sub-total carried to Summary A. |  |  |  | 0
A | SUMMARY A. - MECHANICAL EQUIPMENT ON OZONE
Amount (euro)
I | OZONATION EQUIPMENT
II | LIQUID OXYGEN GASIFICATION STATION
III | MECHANICAL EQUIPMENT
A. | MECHANICAL EQUIPMENT ON OZONE | TOTAL carried to Summary Bill No. 3 |  |  |  | 0
B. | BUILDING WORKS OF OZONE BLOCK
4.1 | TILING WORKS
4.1.1 | Lining concrete pedestals unglazed ceramic tiles, size 10x20 cm. Previously prepared base and lining done carefully. Tiles shall be pointed and cleaned. | see Tehn.spec. 6.1., 16. | 50 | m2
4.1 | TILING WORKS - TOTAL : | Sub-total carried to Summary B. |  |  |  | 0
4.2 | HOUSE AND WOODWORK PAINTING
4.2.1 | Painting the existing metal windows and doors by metal paint, with previous removal of old paint. Prior to painting, remove old paint and corrosion by chemical and physical means, polish and clean. Apply impregnation and primer on windows, and afterwards pre-fill and polish. After applying the first layer of metal paint, fill and polish. Paint the second time by metal paint, in shade according to customer’s choice. | see Tehn.spec. 6.1., 10. | 40 | m2 |  | 0
4.2.2 | Stripping old paint and painting walls and ceilings with semi-dispersive paint. All surfaces are to be stripped and washed from paint. Polish, fill minor damage with plastic putty and fill with emulsion putty. Paint with semi-dispersive paint in two passes. Color shall be by customer's choice. | see Tehn.spec. 6.1., 10. | 495 | m2 |  | 0
4.2 | HOUSE AND WOODWORK PAINTING - TOTAL : | Sub-total carried to Summary B. |  |  |  | 0
4.3 | CONCRETE WORKS
4.3.1 | Improvements of canals
4.3.1.1 | Cleaning concrete surfaces.
| In places where damage of concrete has been noticed in form of protective layer peeling, segregation or poorly executed working joint it shall be necessary to remove damaged concrete. Works to be carried out by hand tool, and afterwards by chase cutting or in some other suitable manner. By taking care not to damage reinforcement, cut groove sides up to the sound concrete. All groove sides and reinforcement are to be dedusted and cleaned from free concrete parts, dirt, grease, and/or to be prepared for applying repair mortar. It is foreseen to use hand tool for scraping 30% of concrete surfaces (wire brushes, stripping knives, etc.) with manual wash. In places where it is possible and where there are larger surfaces instead of hand tool sand blasting of concrete surfaces will be applied. Estimation is that 70% of the total surface that has been foreseen for cleaning can be cleaned by sand blasting. The price shall include only cleaning surface, with placing of scaffold, which shall remain during recovery. | see Tehn.spec. 6.1., 22. | 1 | sum
4.3.1.2 | Recovery by repair mortar and covering with penetrant based coats
Selection of repair material is to be approved by the Engineer. Work procedure to be performed according to manufacturer’s instructions.
| The price shall include recovery of 20% of the total surface. | see Tehn.spec. 6.1., 22. | 110 | m2 |  | 0
4.3 | CONCRETE WORKS - TOTAL | Sub-total carried to Summary B. |  |  |  | 0
B. | SUMMARY B. - BUILDING WORKS OF OZONE BLOCK
Amount (euro)
4.1 | TILING WORKS
4.2 | HOUSE AND WOODWORK PAINTING
4.3 | CONCRETE WORKS
B. | BUILDING WORKS OF OZONE BLOCK TOTAL | TOTAL carried to Summary Bill No. 3 |  |  |  | 0
| SUMMARY Bill No. 3 |  |  |  |  | Amount (euro)
A. | MECHANICAL EQUIPMENT ON OZONE
B. | BUILDING WORKS OF OZONE BLOCK
Bill No. 3 | OZONE BLOCK | Total carried to Grand Summary - PART 1

## Bill No.4 Flocculation
Bill No. 4 - FLOCCULATION AND LAMELLAR SEDIMANTATION TANK
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
A. | MECHANICAL EQUIPMENT
I. | FLOCCULATION EQUIPMENT
1. | Flocculator 1
| Provision, transport and assembly of flocculator 2. The item shall include complete fabrication of stainless steel structural steel work (according to the drawings from design) for applying mixer blades of stainless steel (channel section 4x2 cm) and 4.8 m long, as well as bearings that should be installed according to details of the equipment supplier, with pertaining alternative with double gear speed reducer. Length of the mixer blade 2750 mm. Height 4800 mm. Motor power P = 1.1 kW. Speed gradient 70-40 s. Mixer r.p.m. (min-max) 2 – 10 min-1 Works to be carried out in everything according to valid technical regulations for this type of works. Material for shafts - stainless steel. Material for blades - stainless steel. | see Tehn.spec. 3.1. | 2 | pcs
2. | Flocculator 2
| Provision, transport and assembly of flocculator. The item shall include complete fabrication of stainless steel structural steel work according to the drawings from design) for applying mixer blades of stainless steel (channel section 4x2 cm) and 4.8 m long, as well as bearings that should be installed according to details of the equipment supplier, with pertaining alternative with double gear speed reducer. Length of the mixer blade 4000 mm. Height 4800 mm. Motor power P = 0,75 kW, Speed gradient 30-5 s. Works to be carried out in everything according to the valid technical regulations for this type of works. Material for shafts - stainless steel. Material for blades - stainless steel. | see Tehn.spec. 3.1. | 2 | pcs
3. | Hand driven butterfly valve
Provision, transport and assembly of hand driving butterfly valves. In-built dimensions shall comply with EN 593 (JUS M.C5.005, DIN 3202) Standards. Butterfly valve flanges shall comply with EN 1092 (JUS M.B6.011, DIN 2503) Standards. Valves shall be made of: • casing - alloyed cast steel SG GGG-40 • seat body - austenitic CrNi steel • disk - alloyed cast steel SG GGG-40 • shaft - chromium steel • sealing ring - EPDM • reducer casing - cast steel GG 25 • Anti-corrosion protection - EKB blue color epoxy coating • Anti-corrosion protection - EKB blue color epoxy coating A set of connection material (bolts, nuts and washers) shall be delivered for flanged connections.
3.1. | DN 700 PN 6 | see Tehn.spec. 3.1., 8.5. | 3 | pcs |  | 0
3.2. | DN 800 PN 6 | see Tehn.spec. 3.1., 8.5. | 3 | pcs |  | 0
4 | Expansion joints
Provision, transport and assembly of mantling/dismantling flanges in manholes. In-built dimensions shall comply with JUS (DIN) Standards. Flange connecting dimensions shall comply with EN 1092 (JUS M.B6.011, DIN 2503) Standard. Flange, movable flange and retaining piece shall be made of high-grade cast steel. A set of connection material (bolts, nuts and washers) shall be delivered for flanged connection.
4.1. | DN 700 PN 6 | see Tehn.spec. 3.1., 8.5. | 3 | pcs |  | 0
4.2. | DN 800 PN 6 | see Tehn.spec. 3.1., 8.5. | 3 | pcs |  | 0
5. | Steel flanges
Provision and delivery of steel welding neck flanges, in compliance with EN 1092-2, bores in compliance with DIN 2501, including bolts, nuts, washers and gaskets for connecting the pipeline with fittings.
5.1. | DN 800 PN 10 | see Tehn.spec. 3.1., 8.5. | 6 | pcs |  | 0
5.2. | DN 700 PN 10 | see Tehn.spec. 3.1., 8.5. | 6 | pcs |  | 0
6. | Pipelines and shaped pieces
Provision, transport and assembly of steel pipelines for external pipe connections of settling chamber, flocculator and lamellar tank. Technical specifications for fabrication and delivery of pipes shall comply with JUS C.B5.240 Standard (Welded steel pipes). Steel Č.0361 will be used for fabrication of pipes. Provision, transport and assembly of steel pipeline.
6.1. | DN 700 PN 2.5 d = 7,1 mm G = 124 kg/m | see Tehn.spec. 3.1., 8.4. | 50 | m |  | 0
6.2. | DN 800 PN 2.5 d =8 mm G = 156 kg/m | see Tehn.spec. 3.1., 8.4. | 90 | m |  | 0
I. | FLOCCULATION EQUIPMENT - TOTAL | Sub-total carried to Summary A. |  |  |  | 0
II. | EQUIPMENT IN LAMELLAR TANK
7. | Lamellas
Fabrication, transport and assembly of lamella made of stainless steel with pertaining box-shaped supports also of stainless steel. Characteristics of lamellas: • width 0.9 m • length 1.54 m • thickness 1 mm • lamella inclination 55 • distance between lamellas 8 cm Works to be executed in everything according to the valid technical regulations for this type of works.
| Lamellas of stainless steel | see Tehn.spec. 3.1. | 7000 | pcs |  | 0
8. | Ducts for clarified water outlet
| Fabrication, transport and assembly of ducts for clarified water outlet made of stainless steel, dimensions 300x1200x5500 mm, thickness ca. 5 mm with appropriate stiffeners and two supports. Works to be executed in everything according to the valid technical regulations for this type of works. | see Tehn.spec. 3.1. | 100 | pcs
9. | Overflow bands
| Fabrication, transport and assembly of steel dentil overflow band of stainless steel with guides for adjustment 15 cm wide. Works to be executed in everything according to the valid technical regulations for this type of works. | see Tehn.spec. 3.1. | 1100 | m |  | 0
10. | Intermediate poles of ducts for clarified water outlet
| Fabrication, transport and assembly of the poles of stainless steel DN 150 wall thickness 2 mm and 4 m long. | see Tehn.spec. 3.1., 8.4. | 192 | pcs |  | 0
11. | Pipes for sludge outlet
Fabrication, transport, removal of the existing pipeline and assembly of stainless steel pipeline for sludge outlet.
| DN 100 PN 2.5 d = 2,5 mm G = 4,5 kg/m | see Tehn.spec. 3.1., 8.4. | 150 | m |  | 0
II. | EQUIPMENT IN LAMELLAR TANK - TOTAL | Sub-total carried to Summary A. |  |  |  | 0
A | SUMMARY A. - MECHANICAL EQUIPMENT
Amount (euro)
I | FLOCCULATION EQUIPMENT
II | EQUIPMENT IN LAMELLAR TANK
A. | MECHANICAL EQUIPMENT | TOTAL carried to Summary Bill No. 4 |  |  |  | 0
B. | BUILDING WORKS OF FLOCCULATION FACILITY
1. | PRELIMINARY WORKS
1.1 | Cleaning-up terrain . | see Tehn.spec. 7., 10. | 1 | sum
1.2 | Geodetic marking of the facility, pipeline, etc. | see Tehn.spec. 7., 10. | 1 | sum
1. | TOTAL PRELIMINARY WORKS: | Sub-total carried to Summary B. |  |  |  | 0
2. | EARTHWORKS |  |  |  |  | 0
2.1 | Combined wide cut excavation for facility and pipelines (slope 1:1 and 2:1 - according to drawings), including loading onto vehicles. Approach roads and necessary underpinning are included into unit price. |  |  |  |  | 0
| Prior to commencing excavation works, all preliminary works and geodetic terrain survey with check of levels are to be carried out. |  |  |  |  | 0
Measurement per m3 of excavated earth:
2.1.1 | - manual excavation of II category soil (10 %) | see Tehn.spec. 7., 10. | 480 | m3 |  | 0
2.1.2 | - machine excavation of II category soil (10 %) | see Tehn.spec. 7., 10. | 4320 | m3 |  | 0
2.2 | Removal of the top soil in thickness of 30 cm and its disposal along the trench edge to distance of 1 m minimum, including returning and spreading upon completion of works and backfilling of trench. | see Tehn.spec. 7., 10. | 44.5 | m3
2.3 | Filling up, spreading and compaction of the excavated material (as approved by the Supervisor) around the facility, in layers of 20 cm. Minimum impaction MS=90 MN/m2.
| Prior to filling up, preliminary works and geodetic surveying of terrain, including check of levels are to be carried out. |  |  |  |  | 0
| Measurement per m3 of filled up and compacted material. | see Tehn.spec. 7., 10. | 2050 | m3 |  | 0
2.4 | Provision, transport, filling up, spreading, compacting and fine planning of the layer of hoggin in thickness of 15 cm underneath ground beams, foundation slabs and pavements.
| Measurement per m3. | see Tehn.spec. 7., 10. | 67.5 | m3 |  | 0
2.5 | Provision and laying perforated PVC drain pipe DN 150, in accordance with drawing, including all necessary material and work.
| Measurement per m'. | see Tehn.spec. 7., 10. | 55 | m' |  | 0
2.6 | Deposition and compaction of sand for bed
including provision of material for bed, 15 cm underneath the pipe and 30 cm above the pipe, including compaction of earth up to 10 MN/m2 prior to placing the material for bed. Material for bed shall satisfy pipe manufacturer’s technical requirements.
Measurement per m3 of compacted material.
2.6.1 | - pipeline DN 700 | see Tehn.spec. 7., 10. | 4.2 | m3 |  | 0
2.6.2 | - pipeline DN 800 | see Tehn.spec. 7., 10. | 5 | m3 |  | 0
2.7 | Carting away the excessive earth from trench to landfill specified by the Supervisor, with rough planning on landfill site.
| Measurement per m3 of carted earth. | see Tehn.spec. 7., 10. | 2750 | m3 |  | 0
2. | TOTAL EARTHWORKS | Sub-total carried to Summary B. |  |  |  | 0
3. | ROAD WORKS
3.1 | Placement of asphalt d=4 cm, AB_08 or AB_11 or AB_11s, bituminous coarse aggregate, thickness 4-12 cm, BNS 22B or BNS 32A or BNS 32B and non- bituminous layers (sub-base of vibrated gravel of 0 - 31,5 granulation mm, thickness 25 cm, Me=90MN/m² for construction of road to the facility for mixers (including all necessary work, transport and material).
| Measurement per m2. | see Tehn.spec. 7. | 590 | m2 |  | 0
3. | TOTAL ROAD WORKS: | Sub-total carried to Summary B. |  |  |  | 0
4. | MASONRY WORKS
4.1 | Bricking of external and internal walls, d=25 cm, with face brick, in cement mortar 1:2:6. The price shall include pointing, work, material, scaffolds and equipment.
| Measurement per m3 of wall. | see Tehn.spec. 7., 11. | 46.8 | m3 |  | 0
4. | TOTAL MASONRY WORKS : | Sub-total carried to Summary B. |  |  |  | 0
5. | CONCRETE AND REINFORCED CONCRETE WORKS
A. Mass concrete works
5.1 | Construction of sub-base of mass concrete MB 15 (C 15), underneath facility and manholes foundation slabs. The price shall include all necessary material and works.
5.1.1 | - underneath facility dsl=10 cm | see Tehn.spec. 7., 12. | 332.8 | m2 |  | 0
5.1.2 | - underneath manholes dsl=10 cm | see Tehn.spec. 7., 12. | 34 | m2 |  | 0
5.2 | Construction of footway in width of 1.0 m around the flocculation facility: staircases 2X4x16,5/30 + path (d=10 cm)
| Measurement per m3. | see Tehn.spec. 7., 12. | 10.1 | m3 |  | 0
B. 1 Reinforced concrete works - flocculation facility
5.3 | Construction of reinforced concrete foundation slab (Pos TP1 and Pos TP2) in smooth formwork, dpl=50 cm, MB30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 130.02 | m3
5.4 | Construction of flocculation facility reinforced concrete walls (Pos Z1, Z2, Z3, Z4, Z5, Z6 and Z7) in double smooth formwork, d2 = 40 cm, height 5.7 m, MB30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 244.4 | m3
5.5 | Construction of flocculation facility reinforced concrete upper slabs (Pos PL1 and Pos PL2) in double smooth formwork, dpl=30 cm, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 69.4 | m3
5.6 | Construction of goods loading and unloading platform and staircase in smooth formwork, dpl=20cm, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 8.1 | m3
5.7 | Construction of reinforced concrete walls (Pos Z11) in double smooth formwork, dpl=30 cm, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 4.06 | m3
5.8 | Construction of columns (vertical ring beams), cross section dimensions b/d=40/30 cm, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 6.66 | m3
5.9 | Construction of roof beams, (Pos R1, Pos R2, Pos R21, Pos R22, Pos R23, Pos R23, Pos R3, Pos 31 and Pos R4 ) dg=25 cm, of variable heights 55 cm and 75 cm, in smooth formwork, in accordance with design. The price shall include necessary work, formwork, scaffolds, supports and material. | see Tehn.spec. 7., 12. | 23.7 | m3
5.10 | Construction of semi-prefabricated roof decking (Pos KP1, Pos KP2 and Pos KP3) cast in situ in formwork of precast strips. Blocks shall be TM - 3, dimensions 25 x25x16 cm. | see Tehn.spec. 7., 12. | 121 | m2
B.2 Reinforced concrete works - polyelectrolyte dozing facility
5.11 | Construction of strip foundation (Pos TP1) footing width of 1.0 m, thickness of 30 cm, ground beam width of 25 cm, ground beam height of 1.30 m, length of 5.80 m, MB 30, in everything according to design. The price shall include necessary work, formwork and material. | see Tehn.spec. 7., 12. | 3.65 | m3
5.12 | Construction of strip foundation (Pos TP2) footing width of 0.8 m, thickness 30 cm, ground beam width 25 cm, ground beam height of 1.30 m, MB 30, in everything according to design. The price shall include necessary work, formwork and material. | see Tehn.spec. 7., 12. | 5.06 | m3
5.13 | Construction of reinforced concrete upper slab in double smooth formwork, dpl=20 cm, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 6.4 | m3
5.14 | Construction of columns (vertical ring beams), cross section dimensions b/d=40/30 cm, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 1.4 | m3
5.15 | Construction of roof beams, (Pos R1) dg=25 cm, of variable heights 55 cm and 75 cm, in smooth formwork, in accordance with design. The price shall include necessary work, formwork, scaffolds, supports and material. | see Tehn.spec. 7., 12. | 2 | m3
5.16 | Construction of semi-prefabricated roof decking (Pos KP2) cast in situ in formwork of precast strips. Blocks shall be TM - 3, dimensions 25 x25x16 cm. | see Tehn.spec. 7., 12. | 42 | m2
B.3 Reinforced concrete works - manholes
5.17 | Construction of manhole bottom slab Pos Š1, thickness 20 cm of impermeable concrete V6, MB 30, with necessary formwork. | see Tehn.spec. 7., 12. | 2.5 | m3
5.18 | Construction of manhole reinforced concrete walls Pos Š1 (Pos Z1, Pos Z2, Pos Z3 and Pos Z4), of impermeable concrete V6, MB30, in double formwork, thickness 20 cm (according to design). The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 7., 12. | 5.9 | m3
5.19 | Construction of upper prefabricated slabs of manhole Pos Š1, thickness of 20 cm, dimensions 1m x 2.6 m, in everything according to drawings, of impermeable concrete V6, MB30, with necessary formwork. | see Tehn.spec. 7., 12. | 2.6 | m2
5.20 | Construction of bottom slab of manhole Pos Š1, thickness of 20 cm, of impermeable concrete V6, MB30, with necessary formwork. | see Tehn.spec. 7., 12. | 4.5 | m3
5.21 | Construction of reinforced concrete walls of manhole Pos Š2 (Pos Z21, Pos Z22, Pos Z23 and Pos Z24) of impermeable concrete V6, MB30, in double smooth formwork, thickness of 20 cm (according to drawings). | see Tehn.spec. 7., 12. | 7.25 | m3
5.22 | Construction of upper prefabricated slabs of manhole Pos Š2, thickness of 35 cm, dimensions 0.58m x 3.85 m, with erection hooks Ø 12 in everything according to drawings, of impermeable concrete V6, MB30, with necessary formwork. | see Tehn.spec. 7., 12. | 2.25 | m2
5.23 | Construction of reinforced concrete retaining wall behind facility, MB 30, with necessary formwork (according to drawings). | see Tehn.spec. 7., 12. | 83.85 | m3
5.24 | Provision, delivery and erection of prefabricated concrete members (gutters) for collection of surface water at longitudinal retaining wall. The price shall include all preliminary works, material, etc. | see Tehn.spec. 7., 12. | 80 | m'
5. | TOTAL CONCRETE AND REINFORCED CONCRETE WORKS: | Sub-total carried to Summary B. |  |  |  | 0
6. | REINFORCING WORKS
6.1 | Provision, elongation, cutting, bending and placing of reinforcement in everything according to structural analysis and reinforcement details. Quantities according to theoretical weights in kg.
| RA 400/500 | see Tehn.spec. 7., 13. | 66795 | kg |  | 0
6. | TOTAL REINFORCING WORKS: | Sub-total carried to Summary B. |  |  |  | 0
7. | INSULATING WORKS
7.1 | Coating with penetrant all internal surfaces of concrete walls and slabs in chambers (used material must be approved for potable water).
| Preparation of base and treatment of cuts in case of walls and possible cracks with repair material, according to manufacturer’s instructions, including provision and delivery of all necessary materials, scaffolds and necessary work. | see Tehn.spec. 7., 14. | 1080 | m2
7.2 | Fabrication of hydrocarbon waterproofing (waterproof layer - DPC). The price shall include all necessary work and material.
Hydrocarbon waterproofing shall include:
| cold coat of bitulite, hot coat of bitumin, bituminous PVC plate, thickness 4 mm, the second hot bituminous coat. | see Tehn.spec. 7., 14. | 302 | m2
7.3 | Provision, delivery and placement of styropore as “trapped formwork” between concrete columns and girders at strain spots. Thickness: 3 cm. | see Tehn.spec. 7., 14. | 80.5 | m2
7.4 | Covering of joints with aluminium covering staff at facility contact spots. | see Tehn.spec. 7., 14. | 17.3 | m'
7. | TOTAL INSULATING WORKS: | Sub-total carried to Summary B. |  |  |  | 0
8. | ROOFING WORKS
8.1 | Erection of thermal insulation through moisture barrier and roof waterproofing (by use of mineral wool in thickness of 5 cm) as well as provision of material and roof covering with plasticified profiled aluminium sheet (TR profile) in thickness of 1 mm, on Z sub-construction for fixing aluminium sheet. The price shall include all necessary work and material. | see Tehn.spec. 7., | 302 | m2
8. | TOTAL ROOFING WORKS: | Sub-total carried to Summary B. |  |  |  | 0
9. | METALWORK
Note: All external windows and doors shall be made of anodized aluminium, double-glazed, without thermal break (because the facility is not heated). Dimensions and shape of windows and doors are given in ''Facility Elevations'' drawings, including L-section of the same material as doors and windows frames, including all necessary work and material.
9.1 | Fabrication, provision, delivery, erection and fitting of windows of anodized aluminium according to manufacturer’s instructions and metalwork diagrams..
9.1.1 | - dimensions 292x85 | see Tehn.spec. 7., 15. | 8 | pcs |  | 0
9.1.2 | - dimensions 416x85 | see Tehn.spec. 7., 15. | 6 | pcs |  | 0
9.2 | Fabrication, provision, delivery and fitting of doors of anodized aluminium according to manufacturer's instructions and metalwork diagrams.
| dimensions 200x245 | see Tehn.spec. 7., 15. | 5 | pcs |  | 0
9. | TOTAL METALWORK: | Sub-total carried to Summary B. |  |  |  | 0
10. | SHEET METAL WORKS
10.1 | Fabrication and erection of horizontal drain fall pipes of cross-section 12/12 cm of plasticified galvanized sheet metal in thickness of d = 0.7 mm. | see Tehn.spec. 7., 17. | 91 | m'
10.2 | Fabrication and erection of vertical drain fall pipes of cross-section 12/12 cm of plasticified galvanized sheet metal in thickness of d = 0.7 mm | see Tehn.spec. 7., 17. | 25 | m'
10.3 | Provision, fabrication and erection of flashings on facility lateral end of plasticified aluminium profiled sheet in thickness of d = 0.7 mm, including all necessary material and work. | see Tehn.spec. 7., 17. | 45.5 | m2
10.4 | Provision of material, workshop fabrication and erection of steel covers for openings, final dimensions to be established in situ. Cover is made of two parts, opening dimensions 200x200 cm. Cover frame shall be made of L-section L 50.50.5, cover of steel sheet in thickness of 5 mm. The price shall include all necessary work and material as well as removal of rust by sand blasting, protection against corrosion by coat of oil paint and plasticified final coat. | see Tehn.spec. 7., 17. | 4 | pcs
10.5 | Provision of material and fitting of silicone plug underneath floor expansion strip. | see Tehn.spec. 7., 17. | 12 | m'
10.6 | Fabrication and erection of manhole step irons of cast iron, with protection against corrosion. | see Tehn.spec. 7., 17. | 2 | pcs
10. | TOTAL SHEET METAL WORKS: | Sub-total carried to Summary B. |  |  |  | 0
11. | TILING WORKS
11.1 | Tiling to floors and entry platform with clinker tiles 12/25 cm, resistant to impact and chemicals, class I, on layer of cement mortar 1:3, d=2 cm, including plinth of 10 cm. The price shall include all necessary work and material.
11.1.1 | - floors (measurement per m2 of laid tiles) | see Tehn.spec. 7., 16. | 295.5 | m2 |  | 0
11.1.2 | - plinths - only inside the facility (measurement per m') | see Tehn.spec. 7., 16. | 96 | m' |  | 0
11. | TOTAL TILING WORKS: | Sub-total carried to Summary B. |  |  |  | 0
12. | HOUSE AND WOODWORK PAINTING
12.1 | During the execution of works, it shall be mandatory to clean debris and other dirt emerged while executing house and woodwork painting.
Painting the ceilings in the facility by semi-dispersive paints according to the following description:
-skimming of surfaces by appropriate skimming compound until full smoothness;
-polishing by vitreous paper;
-soaping first time;
-applying gypsum on polished wall;
-pre-painting
-soaping second time;
-basic painting in shade;
-spraying by apparatus1st time;
-spraying by apparatus 2nd time;
Finished surfaces shall be of uniform shade, without brush traces, without paint peeling and wiping.
| Measurement per m2 of painted wall. | see Tehn.spec. 7., 10. | 192 | m2 |  | 0
12. | TOTAL HOUSE AND WOODWORK PAINTING: | Sub-total carried to Summary B. |  |  |  | 0
B | SUMMARY B. - BUILDING WORKS OF FLOCCULATION FACILITY
Amount (euro)
1. | PRELIMINARY WORKS
2. | EARTHWORKS
3. | ROAD WORKS
4. | MASONRY WORKS
5. | CONCRETE AND REINFORCED CONCRETE WORKS
6. | REINFORCING WORKS
7. | INSULATING WORKS
8. | ROOFING WORKS
9. | METALWORK
10. | SHEET METAL WORKS
11. | TILING WORKS
12. | HOUSE AND WOODWORK PAINTING
B. | BUILDING WORKS OF FLOCCULATION FACILITY | TOTAL carried to Summary Bill No. 4
C. | SEDIMENTATION TANK FACILITY - PULSATORS
1. | HOUSE AND WOODWORK PAINTING
1.1 | Painting the perimeter beams by concrete paint with previous stripping the old paint. Paint according to customer’s choice. | see Tehn.spec. 6., 10. | 230 | m2 |  | 0
1.2 | Painting the existing metal fence, by metal paint, with previous removal of old paint. Prior to painting, remove old paint and corrosion by chemical and physical means, polish and clean. Apply impregnation and primer. | see Tehn.spec. 6., 10. | 140 | m1 |  | 0
1.3 | Painting the existing metal windows and doors by metal paint, with previous removal of old paint. Prior to painting, remove old paint and corrosion by chemical and physical means, polish and clean. Apply impregnation and primer on windows, and afterwards pre-fill and polish. After applying the first layer of metal paint, fill and polish. Paint the second time by metal paint, in shade according to customer’s choice. | see Tehn.spec. 6., 10. | 60 | m2 |  | 0
1. | HOUSE AND WOODWORK PAINTING - TOTAL | Sub-total carried to Summary C. |  |  |  | 0
2. | CONCRETE WORKS
2.1 | Recovery of roof beams
2.1.1 | Cleaning concrete surfaces.
| In places where damage of concrete has been noticed in form of protective layer peeling, segregation or poorly executed working joint it shall be necessary to remove damaged concrete. Works to be carried out by hand tool, and afterwards by chase cutting or in some other suitable manner. By taking care not to damage reinforcement, cut groove sides up to the sound concrete. All groove sides and reinforcement are to be dedusted and cleaned from free concrete parts, dirt, grease, and/or to be prepared for applying repair mortar. It is foreseen to use hand tool for scraping 30% of concrete surfaces (wire brushes, stripping knives, etc.) with manual wash. In places where it is possible and where there are larger surfaces instead of hand tool sand blasting of concrete surfaces will be applied. Estimation is that 70% of the total surface that has been foreseen for cleaning can be cleaned by sand blasting. The price shall include only cleaning surface, with placing of scaffold, which shall remain during recovery. | see Tehn.spec. 6., 22. | 1 | sum
2.1.2 | Recovery by repair mortar and covering with penetrant based coats
| Recovery by repair mortar and covering with penetrant-based coats Selection of repair material is to be approved by the Supervisor. Work procedure to be performed according to manufacturer’s instructions. The price shall include recovery of 20% of the total surface. | see Tehn.spec. 6., 22. | 231 | m2
2.3 | Recovery of roof slabs
| First, it is necessary to prepare base. Entire concrete surface is to be cleaned up to base sound and hard surface and its appropriate roughness. Special attention shall be paid to removal of damaged cracked and poorly set concrete layers above corroded reinforcement. If construction has already been recovered, it is necessary to remove already applied mass in case it demonstrates poor adhesion and non-compatibility. After preparation of base, it is necessary to carry out complete protection against corrosion of the reinforcement, which means that reinforcing bars shall be fully cleaned from concrete. For this purpose, cement-based pastes with added corrosion inhibitor and synthetic polymers shall be used. They shall be applied by brush in two coats in the total thickness of 2 mm. Selection of repair material must be approved by the Supervisor. Work procedure is to be carried out according to manufacturer’s instructions. |  | 640 | m2 |  | 0
2.4 | Recovery of channels
2.4.1 | Cleaning concrete surfaces.
| In places where damage of concrete has been noticed in form of protective layer peeling, segregation or poorly executed working joint it shall be necessary to remove damaged concrete. Works to be carried out by hand tool, and afterwards by chase cutting or in some other suitable manner. By taking care that reinforcement is not damaged, groove sides shall be cut up to the sound concrete. All groove sides and reinforcement are to be dedusted and cleaned from free concrete parts, dirt, grease, and/or to be prepared for applying repair mortar. It is foreseen to use hand tool for scraping 30% of concrete surfaces (wire brushes, stripping knives, etc.) with manual washing. In places, where it is possible and where there are larger surfaces instead of hand tool, applied shall be sand blasting of concrete surfaces. Estimation is that 70% of the total surface that has been foreseen for cleaning can be cleaned by sand blasting. The price shall include only cleaning surface, with placing of scaffold, which shall remain during recovery. | see Tehn.spec. 6., 22. | 1 | sum
2.4.2 | Recovery by repair mortar and covering with penetrant-based coats
| Selection of repair material is to be approved by the Supervisor. Work procedure to be performed according to manufacturer’s instructions. The price shall include recovery of 40% of the total surface. | see Tehn.spec. 6., 22. | 215 | m2
2. | CONCRETE WORKS - TOTAL | Sub-total carried to Summary C.
C. | SUMMARY C. - SEDIMENTATION TANK FACILITY - PULSATORS
Amount (euro)
1. | HOUSE AND WOODWORK PAINTING
2. | CONCRETE WORKS
C. | SEDIMENTATION TANK FACILITY - PULSATORS | TOTAL carried to Summary Bill No. 4 |  |  |  | 0
| SUMMARY Bill No. 4 |  |  |  |  | Amount (euro)
A. | MECHANICAL EQUIPMENT
B. | BUILDING WORKS OF FLOCCULATION FACILITY
C. | SEDIMENTATION TANK FACILITY - PULSATORS
Bill No. 4 | FLOCCULATION AND LAMELLAR SEDIMANTATION TANK | Total carried to Grand Summary - PART 1

## Bill No.5 Filters
Bill No. 5 - SAND FILTERS
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
A. | MECHANICAL EQUIPMENT ON SAND FILTERS
1. | EQUIPMENT IN FILTER GALLERY
1.1 | Gate valves on water supply to filters-obturators
Obturators shall consist of rubber bellow which is placed into metal frame fixed to the wall of sand filter. Obturators shall be made of special rubber resistant to the effect of ozone that is present in water. Gate valve is connected with electric-pneumatic control valve actuator placed in control cabinet of the pipe gallery.
| dimensions 800x400 mm | see Tehn.spec. 3.5. | 9 | pcs
1.2 | Butterfly valve with pneumatic drive
Maximum operating pressure of the valve shall be 2.5 bar. In-built dimensions shall comply with EN 558-1 ( DIN 3230) Standards. Connection flanges between which the valve is placed shall be in compliance with EN 1092 (JUS M.B6.011, DIN 2503) Standard. Connection with pneumatic drive shall comply with ISO 5211. Valves shall be made of: • casing - alloyed cast steel SG GGG-40 • seat body - austenitic CrNi steel • disc - alloyed cast steel SG GGG-40 • axle - chromium steel • sealing ring - EPDM • Anti-corrosion protection - EKB blue color epoxy coating
1.2.1 | DN 600 PN 10 | see Tehn.spec. 3.5., 4.1., 8.5. | 9 | pcs
1.2.2 | DN 250 PN 10 | see Tehn.spec. 3.5., 4.1., 8.5. | 9 | pcs
1.2.3 | DN 200 PN 10 | see Tehn.spec. 3.5., 4.1., 8.5. | 18 | pcs
1.3 | Pneumatic drive for butterfly valves
Type of design Symmetric -" Gear-rack" Actuator-valve assembly Direct (without "levers" and couplings) Min. air pressure 4,5 bar ( 25%-of nominal pressure Pn=6 bar) Temperature range -20C ....+80C Possibility of angle adjustment of 90° -4° - 4° Diagram of connection to fittings according to EN ISO 5211 Air supply On both sides (double effect) Diagram of valve connecting according to Norm VDI/VDE 3845 (NAMUR) Operating pressure range 2 - 8,0 bar ATEX-Categoty 94/9/EG IP protection IP67 Operating medium Dry air under pressure, oiled or unoiled Shaft material alloyed steel and adequately protected Cover material EN AC-4600, chromium plated, painted (RAL 5021) Casing material: Aluminium-rolled-extruded protected - hard anodization
1.3.1 | for pneumatic valves DN 600 | see Tehn.spec. 3.5. | 9 | pcs
1.3.2 | for pneumatic valves DN 250 | see Tehn.spec. 3.5. | 9 | pcs
1.3.3 | for pneumatic valves DN 200 | see Tehn.spec. 3.5. | 18 | pcs
1.4 | End switch box
| Connection diagram according to Norm VDI/VDE 3845 (NAMUR) Component shape Round Mounting position Free Switch function Open Operating voltage AC 250 V CE-Mark according to EU-low-voltage -Rules Class of protection against corrosion KBK 3 Protection level IP65 | see Tehn.spec. 3.5. | 27 | pcs
1.5 | Valve island
| Valve design: "Piston-slide" valve with electro-magnetic control Operating pressure: 2, (3)...10 bar ( with internal pilot supply ) -0,9 ...10 bar ( with external pilot supply ) Magnet power at 24V: max. 3W Flow through valve: max. 1400 l/min (1600 l/min) Number of valves in assembly: 6 ( 5+1spare) Valve type: 5/2 -monostable Electro-connection-connector: "Multipol-Stecker" Supply voltage: 24VDC | see Tehn.spec. 3.5. | 9 | pcs
1.6 | Electro-pneumatic positioner
| •Electro-pneumatic position transmitter Purpose for double effect pneumatic actuators Mounting Split system Transmitter-Analyzer Set signal 0/4-20 mA.../0-10V Realized position-transmitter Potentiometer Energy supply Operating pressure 0-6 bar signal necessary air in position 0 Nl/min necessary air in operation 50Nl/min Control medium DIN ISO 8573-1 oil content in air Class 3/max.concentration 1mg/m3 Electric supply 24VDC Protection IP65/EN60529 | see Tehn.spec. 3.5. | 9 | pcs
1.7 | Expansion joints
Provision, transport and assembly of mantling/dismantling flanges in manholes. In-built dimensions shall comply with JUS (DIN) Standards. Flange connecting dimensions shall comply with EN 1092 (JUS M.B6.011, DIN 2503) Standard. Flange, movable flange and retaining piece shall be made of high-grade cast steel. A set of connection material (bolts, nuts and washers) shall be delivered for flange coupling.
1.7.1 | DN 600 PN10 | see Tehn.spec. 3.5., 4.3., 8.5 | 9 | pcs
1.7.2 | DN 250 PN 10 | see Tehn.spec. 3.5., 4.3., 8.5 | 9 | pcs
1.7.3 | DN 200 PN 10 | see Tehn.spec. 3.5., 4.3., 8.5 | 18 | pcs
1.8 | Electromagnetic flowmeter DN 250 PN 10
Technical characteristics: • measuring range is 0-100 l/s • sensitivity threshold 0.1-1.0 mm/s • test pressure 1.5 * NP • operating temperature Tmin = -20 C, Tmax = 60 C • internal transmitter lining: manufacturer's recommendation in accordance with water chemical composition • protection: IP 67 (IEC 529 or DIN 40050) • output signal: current 4-20 mA and pulse • measuring accuracy (v  0.5 m/s measurement error is +/- 0.5 % of flow) Maximum operating pressure for flowmeter is 2.5 bar. In-built dimensions shall comply with JUS (DIN) Standards. Connection dimensions of flowmeter flanges shall be in accordance with EN 1092 (JUS M.B6.011, DIN 2503)) Standard. A set of connection material (bolts, nuts and washers) for flanged connections.
| DN 250 PN10 | see Tehn.spec. 3.5., 4.3., 8.5 | 9 | pcs
1.9 | Filter overflow ducts
Foreseen sand filter overflow ducts shall be of stainless steel. They will be made of stainless steel sheet metal having standard format and surface finish in quality 1.4301 (Č.4580). Sheet metal thickness shall be 3 mm.
| dimensions of sheet metal for overflow duct 5x1 m | see Tehn.spec. 3.4., 3.5. | 8 | pcs
1.10 | Stainless steel flanges
| Provision and delivery of stainless steel welding neck flanges, in compliance with EN 1092-2, bores in compliance with DIN 2501, including bolts, nuts, washers and gaskets for connecting the pipeline with fittings. | see Tehn.spec. 8.5
| DN 600 PN 10 |  | 16 | pcs
| DN 250 PN 10 |  | 32 | pcs
| DN 200 PN 10 |  | 16 | pcs
1.11 | Pipelines and shaped pieces
Provision, transport and assembly of stainless steel pipe lines in pipe gallery. Stainless steel pipes shall be delivered according to ISO/metric dimensions in compliance with EN 10217 ili EN 10216 Standard, and tolerances shall comply with EN ISO 1127 Standard.
| DN 600 PN 2.5 d = 4 mm G = 91.1 kg/m | see Tehn.spec. 4.7., 8.4. | 70 | m
| DN 250 PN 2.5 d = 3 mm G = 23 kg/m | see Tehn.spec. 4.7., 8.4. | 15 | m
| DN 200 PN 2.5 d =2,8 mm G = 16.1 kg/m | see Tehn.spec. 4.7., 8.4. | 140 | m
1. | EQUIPMENT IN FILTER GALLERY - TOTAL | Sub-total carried to Summary A.
2. | EQUIPMENT IN MACHINE ROOM
2.1 | Centrifugal pumps for washing the filters
Pump operating characteristics:
delivery [L/s]: 228
discharge head of pump [m]: 8,7
power [kW]: 30
rated speed [min-1]: 1450
Medium being pumped: potable water; temperature around 20 oC; density 1000 kg/m3.
Arrangement: horizontal mounting.
Materials: in compliance with manufacturer's standards for potable water
| Single-stage centrifugal pumps with volute casing of mono-block design according to ISO 2858. Horizontal intake connection, and vertical delivery directed upwards. | see Tehn.spec. 3.6., 8.3. | 2 | pcs
2.2 | Gate valve (with short body) DN 400 PN 10
Maximum operating pressure shall be 2.5 bar. In-built dimensions shall comply with EN 1171 (JUS M.C5.005, DIN 3202) Standards. Flange connection dimensions shall be in compliance with EN 1092 (JUS M.B6.011, DIN 2503) Standard. A set of connection material (bolts, nuts and washers) shall be delivered for flanged connections.
2.2.1 | DN 400 PN10 | see Tehn.spec. 3.6., 4.2., 8.5. | 4 | pcs
2.2.2 | DN 600 PN 10 | see Tehn.spec. 3.6., 4.2., 8.5. | 1 | pcs
2.3 | Expansion joints
Provision, transport and assembly of mantling/dismantling flanges in manholes. In-built dimensions shall comply with JUS (DIN) Standards. Flange connecting dimensions shall comply with EN 1092 (JUS M.B6.011, DIN 2503) Standard. Flange, movable flange and retaining piece shall be made of high-grade cast steel. A set of connection material (bolts, nuts and washers) shall be delivered for flanged connection.
2.3.1 | DN 400 PN10 | see Tehn.spec. 3.6., 4.3., 8.5. | 2 | pcs
2.3.2 | DN 600 PN10 | see Tehn.spec. 3.6., 4.3., 8.5. | 1 | pcs
2.4. | Non-return flap valve DN 400 PN 10
In-built dimensions shall comply with JUS (DIN) Standards. Housing and shutting-off body shall be made of grey iron, and shaft of corrosion resistant steels. Flange connecting dimensions shall be in compliance with EN 1092 (JUS M.B6.011, DIN 2503) Standard. A set of connection material (bolts, nuts and washers) shall be delivered for flanged connections.
| DN 400 PN10 | see Tehn.spec. 3.6., 4.4., 8.5. | 2 | pcs
2.5 | Electromagnetic flowmeter DN 600 PN 10
Technical characteristics: • measuring range is 0-500 l/s • sensitivity threshold 0.1-1.0 mm/s • test pressure 1.5 * NP • operating temperature Tmin = -20 C, Tmax = 60 C • internal transmitter lining: manufacturer's recommendation in accordance with water chemical composition • protection: IP 67 (IEC 529 or DIN 40050) • output signal: current 4-20 mA and pulse • measuring accuracy (v  0.5 m/s measurement error is +/- 0.5 % of flow) Maximum operating pressure for flowmeter is 2.5 bar. In-built dimensions shall comply with JUS (DIN) Standards. Connection dimensions of flowmeter flanges shall be in accordance with EN 1092 (JUS M.B6.011, DIN 2503)) Standard. A set of connection material (bolts, nuts and washers) for flanged connections.
| DN 600 PN10 | see Tehn.spec. 3.6., 4.5., 8.5. | 1 | pcs
2.6 | Steel flanges
Provision and delivery of steel welding neck flanges, in compliance with EN 1092-2, bores in compliance with DIN 2501, including bolts, nuts, washers and gaskets for connecting the pipeline with fittings.
2.6.1 | DN 600 PN 10 | see Tehn.spec. 8.5. | 4 | pcs
2.6.2 | DN 400 PN 10 | see Tehn.spec. 8.5. | 8 | pcs
2.7 | Pipelines and shaped pieces
Provision, transport and assembly of steel pipelines in filter gallery. Technical specifications for fabrication and delivery of pipes shall comply with JUS C.B5.240 Standard (Welded steel pipes). Steel Č.0361 will be used for fabrication of pipes. Provision, transport and assembly of steel pipeline.
2.7.1 | DN 600 PN 2.5 d = 6.3 mm G = 94.1 kg/m | see Tehn.spec. 4.7., 8.4. | 60 | m
2.7.2 | DN 400 PN 2.5 d = 6.3 mm G = 62.4 kg/m | see Tehn.spec. 4.7., 8.4. | 20 | m
2. | EQUIPMENT IN MACHINE SHOP - TOTAL | Sub-total carried to Summary A.
3. | EQUIPMENT IN SEDIMENTATION TANK
3.1 | Gate valve (with short body) DN 600 PN 10
Maximum operating pressure shall be 2.5 bar. In-built dimensions shall comply with EN 1171 (JUS M.C5.005, DIN 3202) Standards. Flange connection dimensions shall be in compliance with EN 1092 (JUS M.B6.011, DIN 2503) Standard. A set of connection material (bolts, nuts and washers) shall be delivered for flanged connections.
| DN 600 PN 10 | see Tehn.spec. 3.8, 4.2., 8.5. | 2 | pcs
3.2 | Expansion joints DN 600 PN 10
Mantling/dismantling flange is fabricated for maximum operating pressure of 2.5 bar. In-built dimensions shall comply with JUS (DIN) Standards. Flange connecting dimensions shall comply with EN 1092 (JUS M.B6.011, DIN 2503) Standard. Flange, movable flange and retaining piece shall be made of high-grade cast steel. A set of connection material (bolts, nuts and washers) shall be delivered for flanged connection.
| DN 600 PN 10 | see Tehn.spec. 3.8, 4.3., 8.5. | 2 | pcs
3.3 | Floating overflow DN 600 with flexible hose DN 300
Floating overflow with flexible hose for discharge of precipitated water from sedimentation tank inflow chamber to discharge chamber.
| floating overflow | see Tehn.spec. 3.8. | 2 | pcs
3.4 | Pipelines and shaped pieces
Provision, transport and assembly of steel pipelines in sedimentation tank. Technical specifications for fabrication and delivery of pipes shall comply with JUS C.B5.240 Standard (Welded steel pipes). Steel Č.0361 will be used for fabrication of pipes. Provision, transport and assembly of steel pipeline.
| DN 600 PN 2.5 d = 6.3 mm G = 94.1 kg/m | see Tehn.spec. 4.7., 8.4. | 10 | m
3.5 | Steel flanges
Provision and delivery of steel welding neck flanges, in compliance with EN 1092-2, bores in compliance with DIN 2501, including bolts, nuts, washers and gaskets for connecting the pipeline with fittings.
| DN 600 PN 10 | see Tehn.spec. 4.7., 8.5. | 4 | pcs
3.6 | Laying the pipeline DN 600
Provision, transport and laying the steel pipeline DN 600 from Kruševac - Brus trunk road to sedimentation tanks. The item shall include combined trench excavation, placement and compaction of sand for bed, trench backfilling with material from excavation and carting away the excessive earth.
| DN 600 PN 2.5 d = 6.3 mm G = 94.1 kg/m | see Tehn.spec. 4.7., 8.4. | 250 | m
3. | EQUIPMENT IN MACHINE SHOP - TOTAL | Sub-total carried to Summary A.
4. | REPLACEMENT OF FILTER MEDIA AND NOZZLES
4.1 | Bearing gravel layer
| Provision and replacement of bearing gravel layer with characteristics: dsr  2,0-3,15 mm | see Tehn.spec. 3.4. | 55 | m3
4.2 | Sand media
| Provision and replacement of filter sand media of the following characteristics: quartz sand: Cunif  1,4 dsr  1-1,2 mm | see Tehn.spec. 3.4. | 410 | m3
4.3 | Anthracite media
| Provision and insertion of filter anthracite media of the following characteristics: type hidrocit dsr ~ 1,4 - 2,6 mm | see Tehn.spec. 3.4. | 155 | m3
4.4 | Filter nozzles
| Provision and replacement of filter nozzles made of special plastics. Taking into account that plastic nozzle brackets are fitted into concrete slabs, only neck nozzles of the following characteristics shall be provided: - width 0,5 mm - number 36 | see Tehn.spec. 3.4. | 28000 | pcs
4. | REPLACEMENT OF FILTER MEDIA AND NOZZLES - TOTAL | Sub-total carried to Summary A.
A | SUMMARY A. - MECHANICAL EQUIPMENT ON SAND FILTERS
Amount (euro)
1. | EQUIPMENT IN FILTER GALLERY
2. | EQUIPMENT IN MACHINE ROOM
3. | EQUIPMENT IN SEDIMENTATION TANK
4. | REPLACEMENT OF FILTER MEDIA AND NOZZLES
A. | MECHANICAL EQUIPMENT ON SAND FILTERS | TOTAL carried to Summary Bill No. 5
B. | BUILDING WORKS ON SAND FILTER FACILITY
1. | HOUSE AND WOODWORK PAINTING
1.1 | Painting the perimeter beams by concrete paint with previous removal of old paint. Paint according to customer’s choice. | see Tehn.spec. 6., 10. | 200 | m2
1.2 | Painting the existing metal fence, by metal paint, with previous removal of the old paint. Prior to painting, remove old paint and corrosion by chemical and physical means, polish and clean. Apply impregnation and primer. | see Tehn.spec. 6., 10. | 140 | m1
1.3 | Painting the existing metal windows and doors, by metal paint, with previous removal of old paint. Prior to painting, remove old paint and corrosion by chemical and physical means, polish and clean. Apply impregnation and primer on windows, and afterwards pre-fill and polish. After applying the first layer of metal paint, fill and polish. Paint the second time by metal paint, in shade according to customer’s choice. | see Tehn.spec. 6., 10. | 87 | m2
1.4 | Provision and gluing the foil to window glass for protection against excessive light in filter gallery. | see Tehn.spec. 6., 10. | 87 | m2
1. | HOUSE AND WOODWORK PAINTING - TOTAL | Sub-total carried to Summary B.
2. | CONCRETE WORKS
2.1 | Recovery of roof beams
2.1.1 | Cleaning concrete surfaces.
| In places where damage of concrete has been noticed in form of protective layer peeling, segregation or poorly executed working joint it shall be necessary to remove damaged concrete. Works to be carried out by appropriate hand tool, and afterwards by chase cutting or in some other suitable manner. By taking care not to damage reinforcement, groove sides shall be cut up to the sound concrete. All groove sides and reinforcement are to be dedusted and cleaned from free concrete parts, dirt, grease, and/or to be prepared for applying repair mortar. It is foreseen to use hand tool for scraping 30% of concrete surfaces (wire brushes, stripping knives, etc.) with manual wash. In places where it is possible and where there are larger surfaces instead of hand tool sand blasting of concrete surfaces will be applied. Estimation is that 70% of the total surface that has been foreseen for cleaning can be cleaned by sand blasting. The price shall include only cleaning of surface, with placing of scaffold, which shall remain during recovery. | see Tehn.spec. 6., 22. | 1 | sum
2.2 | Recovery by repair mortar and covering with penetrant based coats
Selection of repair material is to be approved by the Supervisor. Work procedure to be performed according to manufacturer’s instructions.
| The price shall include recovery of 20% of the total surface. | see Tehn.spec. 6., 22. | 340 | m2
2.3 | Recovery of roof slabs
2.3.1 | First, it is necessary to prepare base. Entire concrete surface is to be cleaned up to sound and hard surface of base and its appropriate roughness. Special attention shall be paid to removal of damaged cracked and poorly set concrete layers above corroded reinforcement. If construction has already been recovered, it is necessary to remove already applied mass in case it demonstrates poor adhesion and non-compatibility. After preparation of base, it is necessary to carry out complete reinforcement protection against corrosion , which means that reinforcing bars shall be completely cleaned from concrete. For this purpose, cement-based pastes with added corrosion inhibitor and synthetic polymers shall be used. They shall be applied by brush in two coats in the total thickness of 2 mm. Selection of repair material must be approved by the Supervisor. Work procedure is to be carried out according to manufacturer’s instructions. | see Tehn.spec. 6., 22. | 720 | m2
2.4 | Recovery of channels
2.4.1 | Cleaning concrete surfaces.
| In places where damage of concrete has been noticed in form of protective layer peeling, segregation or poorly executed working joint it shall be necessary to remove damaged concrete. Works to be carried out by appropriate hand tool, and afterwards by chase cutting or in some other suitable manner. By taking care not to damage reinforcement, groove sides shall be cut up to the sound concrete. All groove sides and reinforcement are to be dedusted and cleaned from free concrete parts, dirt, grease, and/or to be prepared for applying repair mortar. It is foreseen to use hand tool for scraping 30% of concrete surfaces (wire brushes, stripping knives, etc.) with manual wash. In places where it is possible and where there are larger surfaces instead of hand tool sand blasting of concrete surfaces will be applied. Estimation is that 70% of the total surface that has been foreseen for cleaning can be cleaned by sand blasting. The price shall include only cleaning of surface, with placing of scaffold, which shall remain during recovery. | see Tehn.spec. 6., 22. | 1 | sum
2.4.2 | Recovery by repair mortar and covering with penetrant-based coats
Selection of repair material is to be approved by the Supervisor. Work procedure to be performed according to manufacturer’s instructions.
| The price shall include recovery of 40% of the total surface. | see Tehn.spec. 6., 22. | 215 | m2
2. | CONCRETE WORKS - TOTAL | Sub-total carried to Summary B.
3. | EXPANSION JOINT:
Recovery of expansion joint.
3.1 | Cleaning concrete surfaces/
3.1.1 | In places where damage of concrete has been noticed in form of protective layer peeling, segregation or poorly executed working joint it shall be necessary to remove damaged concrete. Works to be carried out by hand tool, and afterwards by chase cutting or in some other suitable manner. By taking care not to damage reinforcement, groove sides shall be cut up to the sound concrete. All groove sides and reinforcement are to be dedusted and cleaned from free concrete parts, dirt, grease, and/or to be prepared for applying repair mortar. It is foreseen to use hand tool for scraping 30% of concrete surfaces (wire brushes, stripping knives, etc.) with manual wash. In places where it is possible and where there are larger surfaces instead of hand tool sand blasting of concrete surfaces will be applied. Estimation is that 70% of the total surface that has been foreseen for cleaning can be cleaned by sand blasting. The price shall include only cleaning of surface, with placing of scaffold, which shall remain during recovery. | see Tehn.spec. 6., 22. | 1 | sum
3.1.2 | Recovery of internal side of damaged surface.
| Selection of repair material should be approved by the Supervisor. Work procedure is to be carried out according to manufacturer’s instructions. | see Tehn.spec. 6., 22. | 10.2 | m2
3.1.3 | Recovery of external side of damaged surface.
| First, it is necessary to prepare base. Entire concrete surface is to be cleaned up to base sound and hard surface and its appropriate roughness. Special attention shall be paid to removal of damaged cracked and poorly set concrete layers above corroded reinforcement. If construction has already been recovered, it is necessary to remove already applied mass in case it demonstrates poor adhesion and non-compatibility. After preparation of base, it is necessary to carry out complete protection against corrosion of the reinforcement, which means that reinforcing bars shall be fully cleaned from concrete. For this purpose, cement-based pastes with added corrosion inhibitor and synthetic polymers shall be used. They shall be applied by brush in two coats in the total thickness of 2 mm. Selection of repair material must be approved by the Supervisor. Work procedure is to be carried out according to manufacturer’s instructions. | see Tehn.spec. 6., 22. | 12.2 | m2
3. | EXPANSION JOINT: | Sub-total carried to Summary B.
B. | SUMMARY B. - BUILDING WORKS ON SAND FILTER FACILITY
Amount (euro)
1. | HOUSE AND WOODWORK PAINTING
2. | CONCRETE WORKS
3. | EXPANSION JOINT:
B. | BUILDING WORKS ON SAND FILTER FACILITY | TOTAL carried to Summary Bill No. 5
| SUMMARY Bill No. 5 |  |  |  |  | Amount (euro)
A. | MECHANICAL EQUIPMENT ON SAND FILTERS
B. | SUMMARY B. - BUILDING WORKS ON SAND FILTER FACILITY
Bill No. 5 | SAND FILTERS | Total carried to Grand Summary - PART 1

## Bill No. 6 UV disinfection
Bill No. 6 - UV DISINFECTION
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
A. | UV DISINFECTION SYSTEM
1. | UV DISINFECTION
UV disinfection - it has been foreseen that UV disinfection shall follow the two-layer sand-anthracite filters. The most efficient range is germicidal spectrum range and/or UV radiation range of 200 - 300 nm. In accordance with plant capacity of 3600 m3/h, for UV radiation two UV units have been adopted in operation and one standby, each having capacity of 2120 m3/h. Adopted UV disinfection is a disinfection of high efficiency with low power consumption and high UV-C outlet (200-280 nm). It can be used in the range of 0-60 °C.
UV system of the following characteristics has been foreseen: • maximum flow 2120 m3/h • inlet diameter DN 500 • installed power 11,6 kW • dimensions W 1060 x H 2400 x D 1380 mm • multi-lamp system • dosage 400 J/m2 • made of stainless steel with concentric UV lamp arrangements
1.1. | UV reactor • material - stainless steel • valve diameter DN 500 • weight 1050 kg • capacity approx. 1540 l • temperature 5 - 60 °C • operating pressure 10 bar • protection type IP 65 | see Tehn.spec. 3.8. | 3 | pcs
1.2. | UV lamps (32 per reactor) • lamp power approx. 330 W • UV-C outlet approx. 150 W • minimum lamp duration 12 000 h | see Tehn.spec. 3.8. | 96 | pcs
1.3. | Protective lamp ring (32 per reactor) • made of hard quartz | see Tehn.spec. 3.8. | 96 | pcs
1.4. | UV sensor (1 per reactor) • accuracy ± 3 %, selectivity > 99 % | see Tehn.spec. 3.8. | 3 | pcs
1.5. | Electrical cabinet (1 per reactor) • dimensions 1200 x 1900 x 600 • installed power 11,6 kW | see Tehn.spec. 3.8. | 3 | pcs
1. | UV DISINFECTION - TOTAL | Sub-total carried to Summary A.
2. | MECHANICAL EQUIPMENT
2.1 | Butterfly valve with electro drive with possibility of manual opening/closing
Butterfly valve with seat of flexible material, with double eccentricity, design and type according to EN593. In-built dimensions shall comply with EN 558-1 (DIN 3230). Connection flanges between which the valve is placed shall be in compliance with EN 1092 (JUS M.B6.011, DIN 2503) Standard. Valves shall be made of: • casing - alloyed cast steel SG GGG-40 • seat body - austenitic CrNi steel • disc - alloyed cast steel SG GGG-40 • axle - chromium steel • sealing ring - EPDM • reducer casing - cast steel GG 25 • Anti-corrosion protection - EKB blue color epoxy coating • Anti-corrosion protection - EKB blue color epoxy coating A set of connection material (bolts, nuts and washers) shall be delivered for flanged connections.
2.1.1 | DN 1000 PN 10 | see Tehn.spec. 8.5. | 2 | pcs
2.1.2 | DN 700 PN 10 | see Tehn.spec. 8.5. | 6 | pcs
2.2 | Expansion joints
Provision, transport and assembly of mantling/dismantling flanges. In-built dimensions shall comply with JUS (DIN) Standards. Flange connecting dimensions shall comply with EN 1092 (JUS M.B6.011, DIN 2503) Standard. Flange, movable flange and retaining piece shall be made of high-grade cast steel. A set of connection material (bolts, nuts and washers) shall also be delivered for flanged connection.
| DN 1000 PN10 | see Tehn.spec. 8.5. | 2 | pcs
2.3 | Pipelines and shaped pieces
Provision, transport and assembly of steel pipelines for connecting UV disinfection system. Technical specifications for fabrication and delivery of pipes shall comply with JUS C.B5.240 Standard (Welded steel pipes). Steel Č.0361 will be used for fabrication of pipes. Provision, transport and assembly of steel pipeline.
2.3.1 | DN 1000 PN 6 d = 10 mm G = 248 kg/m | see Tehn.spec. 8.4. | 10 | m
2.3.2 | DN 800 PN 6 d = 8 mm G = 158 kg/m | see Tehn.spec. 8.4. | 15 | m
2.3.3 | DN 700 PN 6 d =7,1 mm G = 124 kg/m | see Tehn.spec. 8.4. | 30 | m
2.4 | Steel flanges
Provision and delivery of steel welding neck flanges, in compliance with EN 1092-2, bores in compliance with DIN 2501, including bolts, nuts, washers and gaskets for connecting pipeline with fittings.
2.4.1 | DN 1000 PN 10 | see Tehn.spec. 8.5. | 4 | pcs
2.4.2 | DN 700 PN 10 | see Tehn.spec. 8.5. | 12 | pcs
2.4.3 | DN 500 PN 6 | see Tehn.spec. 8.5. | 12 | pcs
2. | MECHANICAL EQUIPMENT - TOTAL | Sub-total carried to Summary A.
A | SUMMARY A. - MECHANICAL EQUIPMENT FOR UV DISINFECTION
Amount (euro)
1. | UV DISINFECTION
2. | MECHANICAL EQUIPMENT
A. | MECHANICAL EQUIPMENT FOR UV DISINFECTION | TOTAL carried to Summary Bill No. 6
B. | BUILDING WORKS OF UV DISINFECTION
1. | PRELIMINARY WORKS
1.1 | Terrain clean-up. | see Tehn.spec. 10. | 1 | sum
1.2 | Geodetic marking of the facility, pipeline, etc. | see Tehn.spec. 10. | 1 | sum
1. | PRELIMINARY WORKS - TOTAL | Sub-total carried to Summary B.
2. | EARTHWORKS
2.1 | Combined wide cut excavation for facility, including loading onto vehicles. Approach roads and necessary underpinning are included into unit price.
Prior to commencing excavation works, all preliminary works and geodetic terrain survey with check of levels are to be carried out.
Measurement per m3 of excavated earth:
2.1.1 | - manual excavation of II category soil (10 %) | see Tehn.spec. 10. | 114 | m3
2.1.2 | - machine excavation of II category soil (10 %) | see Tehn.spec. 10. | 1140 | m3
2.2 | Removal of the top soil in thickness of 30 cm and its disposal along the trench edge to distance of 1 m minimum, including returning and spreading upon completion of works and backfilling of trench. | see Tehn.spec. 10. | 172 | m3
2.3 | Filling up, spreading and compaction of the excavated material from excavation (as approved by the Engineer) around the facility, in layers of 20 cm. Minimum impaction MS=90 MN/m2.
Prior to filling up, preliminary works and geodetic surveying of terrain, including check of levels are to be carried out.
| Measurement per m3 of filled up and compacted material. | see Tehn.spec. 10. | 560 | m3
2.4 | Provision, transport, filling up, spreading, compacting and fine planning of the layer of hoggin in thickness of 15 cm underneath foundation slab and pavement.
| Measurement per m3. | see Tehn.spec. 10. | 45 | m3
2.5 | Carting away the excessive earth from excavation to landfill specified by the Engineer, with rough planning on landfill site.
| Measurement per m3. | see Tehn.spec. 10. | 663 | m3
2. | EARTHWORKS - TOTAL | Sub-total carried to Summary B.
3. | MASONRY WORKS
3.1 | Bricking of external walls, d=25 cm, with face brick, in cement mortar 1:2:6. The price shall include pointing, work, material, scaffolds and equipment.
| Measurement per m3. | see Tehn.spec. 11. | 36 | m3
3. | MASONRY WORKS - TOTAL | Sub-total carried to Summary B.
4. | CONCRETE AND REINFORCED CONCRETE WORKS
A. Mass concrete works
4.1 | Construction of sub-base of mass concrete MB 15 (C 15), underneath facility foundation slab. The price shall include all necessary material and works.
| - underneath facility dsl=10 cm | see Tehn.spec. 12. | 440 | m2
B. 1 Reinforced concrete works
4.2 | Construction of reinforced concrete foundation slab in smooth formwork, dpl=35 cm, MB30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 12. | 68 | m3
4.3 | Construction of reinforced concrete walls in double smooth formwork, dz=30 cm, of height 2.8 m, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork concreting and curing. | see Tehn.spec. 12. | 50 | m3
4.4 | Construction of reinforced concrete upper slab in double smooth formwork, dpl cm, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 12. | 8 | m3
4.5 | Construction of columns (vertical ring beams), cross section dimensions b/d=30/30 cm, MB 30, impermeability grade V6, in accordance with design. The price shall include fabrication and placement of formwork, concreting and curing. | see Tehn.spec. 12. | 3.5 | m3
4.6 | Construction of roof beams, dg=25 cm, in smooth formwork, in accordance with design. The price shall include necessary work, formwork, scaffolds, supports and material. | see Tehn.spec. 12. | 18 | m3
4.7 | Construction of semi-prefabricated roof decking cast in situ in formwork of precast strips. Blocks shall be TM - 3, dimensions 25 x25x16 cm. | see Tehn.spec. 12. | 240 | m2
4. | CONCRETE AND REINFORCED CONCRETE WORKS - TOTAL | Sub-total carried to Summary B.
5. | REINFORCING WORKS
5.1 | Provision, straightening, cutting, bending and placing of reinforcement in everything according to structural analysis and reinforcement details. Quantities according to theoretical weights in kg.
| RA 400/500 | see Tehn.spec. 13. | 20000 | kg
5. | REINFORCING WORKS - TOTAL | Sub-total carried to Summary B.
6. | INSULATING WORKS
6.1 | Coating with penetrant of all internal surfaces of concrete walls and slabs in chambers.
| Preparation of base and treatment of cuts in case of walls and possible cracks with repair material, according to manufacturer’s instructions, including provision and delivery of all necessary materials, scaffolds and necessary work. | see Tehn.spec. 14. | 352 | m2
6.2 | Fabrication of hydrocarbon waterproofing (waterproof layer - DPC). The price shall include all necessary work and material.
Hydrocarbon waterproofing shall include:
| cold coat of bitulite, hot coat of bitumin, bituminous PVC plate, thickness 4 mm, the second hot bituminous coat. | see Tehn.spec. 14. | 248 | m2
6. | INSULATING WORKS - TOTAL | Sub-total carried to Summary B.
7. | ROOFING WORKS
7.1 | Erection of thermal insulation through moisture barrier and roof waterproofing (by use of mineral wool in thickness of 5 cm) as well as provision of material and roof covering with plasticified profiled aluminium sheet (TR profile) in thickness of 1 mm, on Z sub-construction for fixing aluminium sheet. The price shall include all necessary work and material. |  | 248 | m2
7. | ROOFING WORKS - TOTAL | Sub-total carried to Summary B.
8. | METALWORK
| Note: All external windows and doors shall be made of anodized aluminium, double-glazed, without thermal break (because the facility is not heated). | see Tehn.spec. 15.
8.1 | Fabrication, provision, delivery, erection and fitting of windows of anodized aluminium according to manufacturer’s instructions and metalwork diagrams..
| - dimensions 292x85 | see Tehn.spec. 15. | 11 | pcs
8.2 | Fabrication, provision, delivery and fitting of doors of anodized aluminium according to manufacturer's instructions and metalwork diagrams.
| - dimensions 300x245 | see Tehn.spec. 15. | 1 | pcs
8. | METALWORK - TOTAL | Sub-total carried to Summary B.
9. | SHEET METAL WORKS
9.1 | Fabrication and erection of horizontal drain fall pipes of cross-section 12/12 cm of plasticified galvanized sheet metal in thickness of d = 0.7 mm. | see Tehn.spec. 17. | 56 | m'
9.2 | Fabrication and erection of vertical drain fall pipes of cross-section 12/12 cm of plasticified galvanized sheet metal in thickness of d = 0.7 mm | see Tehn.spec. 17. | 12 | m'
9.3 | Provision, fabrication and erection of flashings on facility lateral end of plasticified aluminium profiled sheet in thickness of d = 0.7 mm, including all necessary material and work. | see Tehn.spec. 17. | 12 | m2
9.4 | Fabrication and erection of machine shop step irons of cast iron, with protection against corrosion. | see Tehn.spec. 17. | 4 | pcs
9. | SHEET METAL WORKS - TOTAL | Sub-total carried to Summary B.
10. | TILING WORKS
10.1 | Tiling to machine shop floors and gallery with clinker tiles 12/25 cm, resistant to impact, class I, on layer of cement mortar 1:3, d=2 cm, including plinth of 10 cm. The price shall include all necessary work and material.
10.1.1 | - floors (measurement per m2 of laid tiles) | see Tehn.spec. 16. | 240 | m2
10.1.2 | - plinths - only inside the facility (measurement per m') | see Tehn.spec. 16. | 74 | m'
10. | TILING WORKS - TOTAL | Sub-total carried to Summary B.
11. | HOUSE AND WOODWORK PAINTING
11.1 | During the execution of works, it shall be mandatory to clean debris and other dirt emerged while executing painting works.
Painting the ceilings in the facility by semi-dispersive paints according to the following description:
-skimming of surfaces by appropriate skimming compound until full smoothness;
-polishing by vitreous paper;
-soaping 1st time;
-applying gypsum on polished wall;
-pre-painting
-soaping 2nd time;
-basic painting in shade;
-spraying by apparatus1st time;
-spraying by apparatus 2nd time;
Finished surfaces shall be of uniform shade, without brush traces, without paint peeling and paint wiping.
| Measurement per m2 of painted wall. | see Tehn.spec. 10. | 232 | m2
11. | HOUSE AND WOODWORK PAINTING - TOTAL | Sub-total carried to Summary B.
B | SUMMARY B. - BUILDING WORKS OF UV DISINFECTION
Amount (euro)
1. | UV DISINFECTION
2. | MECHANICAL EQUIPMENT
3. | MASONRY WORKS
4. | CONCRETE AND REINFORCED CONCRETE WORKS
5. | REINFORCING WORKS
6. | INSULATING WORKS
7. | ROOFING WORKS
8. | METALWORK
9. | SHEET METAL WORKS
10. | TILING WORKS
11. | HOUSE AND WOODWORK PAINTING
B. | BUILDING WORKS OF UV DISINFECTION | TOTAL carried to Summary Bill No. 6
| SUMMARY Bill No. 6 |  |  |  |  | Amount (euro)
A. | UV DISINFECTION SYSTEM
B. | BUILDING WORKS OF UV DISINFECTION
Bill No. 6 | SAND FILTERS | Total carried to Grand Summary - PART 1

## Bill No.7 Office Block
Bill No.7 - BUILDING WORKS - ADMINISTRATIVE BUILDING
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
I | BUILDING WORKS - ADMINISTRATIVE BUILDING
1. | DISMANTLING AND DEMOLITION
1.1. | Removal of the existing equipment from rooms being reconstructed. | see Tehn.spec. 6., 21. | 1 | sum
1.2 | Careful dismantling metal single-wing windows, dimensions 150x170 cm. Dismantled windows are to be loaded onto truck and carted away to landfill. | see Tehn.spec. 6., 21. | 75 | pcs
1.3 | Careful dismantling metal single-wing wooden doors together with door frame and threshold. Dismantled doors are to be loaded onto truck and carted away to landfill. | see Tehn.spec. 6., 21. | 50 | pcs
1.4 | Removal of floor ceramic tiles. Break off tiles and remove base up to concrete structure. Collect debris, take it out, load it onto truck and cart away to town landfill. | see Tehn.spec. 6., 21. | 26 | m2
1.5 | Breaking off the wall ceramic tiles together with mortar. Collect debris, take it out, load it onto truck and cart away to town landfill. | see Tehn.spec. 6., 21. | 82 | m2
1.6 | Demolition of staircase covering of terrazzo with base. | see Tehn.spec. 6., 21. | 5 | m2
1.7 | Dismantling the sanitary ware in sanitary knots. Dismantle sanitary ware and cart away to landfill by the Supervisor's choice.
1.7.1 | water taps | see Tehn.spec. 6., 21. | 15 | pcs
1.7.2 | shower taps | see Tehn.spec. 6., 21. | 8 | pcs
1.7.3 | wash basins | see Tehn.spec. 6., 21. | 12 | pcs
1.7.4 | shower baths | see Tehn.spec. 6., 21. | 8 | pcs
1.7.5 | WC pans, flushing cistern and pipes | see Tehn.spec. 6., 21. | 9 | pcs
1.8 | Careful dismantling boilers. Dismantle water heaters and cart away to landfill by the Supervisor's choice.
| water heater | see Tehn.spec. 6., 21. | 12 | pcs
1.9 | Dismantling water supply network of anodized pipes. Load and cart away to landfill by the Supervisor's choice. | see Tehn.spec. 6., 21. | 72 | m1
1. | DISMANTLING AND DEMOLITION - TOTAL | TOTAL carried to Summary Bill No. 7
2. | TILING WORKS
2.1 | Tiling to wall ceramic tiles, dimensions 20x30 cm, onto adhesive, in bond joint to joint. Faced surfaces shall be flat and vertical. Tiles shall be pointed and cleaned. The price shall also include provision of tiles. Color of tiles shall be by customer's choice. | see Tehn.spec. 6., 16. | 82 | m2
2.2 | Tiling to floor ceramic tiles, dimensions 20x30 cm, in cement mortar. Tiles of class I shall be in bond joint to joint. Faced surfaces shall be flat and vertical. Tiles shall be pointed and cleaned. The price shall also include provision of tiles. Color of tiles shall be by customer's choice. | see Tehn.spec. 6., 16. | 26 | m2
2. | TILING WORKS - TOTAL | TOTAL carried to Summary Bill No. 7
3. | STONE MASON'S WORKS
3.1 | Tailing to floor marble tiles, dimensions 30x30x2, in entry to the facility. Tiles shall be tilled in cement mortar in ratio 1:3, clean joints and stone. Marble type and color shall be by customer's choice. The price shall also include preparation of base and pointing. | see Tehn.spec. 6., 16. | 5 | m2
3. | STONE MASON'S WORKS - TOTAL | TOTAL carried to Summary Bill No. 7
4. | HOUSE AND WOODWORK PAINTING
4.1 | Stripping old paint and painting walls and ceilings with semi-dispersive paint. All surfaces are to be stripped and washed from paint. Polish, fill minor damage with plastic putty and fill with emulsion putty. Paint with semi-dispersive paint in two passes. Color shall be by customer's choice. | see Tehn.spec. 6., 10. | 3000 | m2
4.2 | Painting the existing metal doors by metal paint, with previous removal of old paint. Prior to painting, remove old paint and corrosion by chemical and physical means, polish and clean. Apply impregnation and primer on windows, and afterwards pre-fill and polish. After applying the first layer of metal paint, fill and polish. Paint the second time by metal paint, in shade by customer’s choice. | see Tehn.spec. 6., 10. | 10 | m2
4.3 | Dismantling and painting metal radiators by metal paint, with previous removal of old paint. Prior to painting remove old paint and corrosion by chemical and physical means, polish and clean. The price shall also include mounting of painted radiators. | see Tehn.spec. 6., 10. | 100 | m2
4. | HOUSE AND WOODWORK PAINTING - TOTAL | TOTAL carried to Summary Bill No. 7
5. | METALWORK
5.1 | Fabrication, mounting and fitting anodized aluminium windows in everything according to manufacturer's detail and metalwork diagram.
| Dim.150/170 | see Tehn.spec. 6., 15. | 72 | pcs
5.2 | Placing venetian blinds of aluminium lamellas, width 16 mm, by customer's choice. Blinds shall be fitted with mechanism for lifting, lowering and adjusting lamella tilt. | see Tehn.spec. 6., 15. | 184 | m2
5. | METALWORK - TOTAL | TOTAL carried to Summary Bill No. 7
6. | JOINERY WORKS
6.1 | Fabrication and placing single-wing internal double hollow-core doors without hopper window. Doors are to be made of first class and dry fir and spruce, and frame construction of wings shall be faced with plywood in thickness of 4 mm. Door frame shall be in the width of wall and trimmed. Place door finish hardware of anodized aluminium, mortise lock with one key, three laid-in hinges per wing by customer's choice. Doors shall be protected by colorless impregnation coat. A rubber stop shall be placed on floor.
6.1.1 | Dim. 90/205 | see Tehn.spec. 6., 18. | 35 | pcs
6.1.2 | Dim. 70/205 | see Tehn.spec. 6., 18. | 15 | pcs
6.2 | Fabrication and placing kitchen cabinets of chipboard and medium density fiberboard. Framing shall be made of melamine-surfaced chipboard, doors and drawer faces of medium density fiberboard. Fitting-in double bowl dishwasher of stainless steel with associated connections to sewerage.
6.2.1 | wall cupboards of height up to 90 cm | see Tehn.spec. 6., 18. | 10 | m1
6.2.2 | working base units | see Tehn.spec. 6., 18. | 10 | m1
6.2.3 | double bowl dishwasher with hot and cold-water taps | see Tehn.spec. 6., 18. | 2 | pcs
6. | JOINERY WORKS - TOTAL | TOTAL carried to Summary Bill No. 7
7. | INTERNAL WATER SUPPLY NETWORK AND SEWERAGE
7.1 | Provision and assembly of PVC water pipes, together with pipe fitting and connection material. Chase cutting for fitting and passage of pipes shall be carried out carefully. Care shall be taken that valve roses and tap are completely flat with final wall surface.
7.1.1 | 1/2" |  | 42 | m1
7.1.2 | 3/4" |  | 12 | m1
7.2 | Provision and assembly of PVC drain pipe for internal sewerage together with shaped pieces and connection material.
7.2.1 | Ø50 |  | 10 | m1
7.2.2 | Ø100 |  | 5 | m1
7.2.3 | gullies 100 mm |  | 15 | pcs
7.3 | Provision and mounting sanitary ware completely for all floors.
7.3.1 | one-handed water taps |  | 15 | pcs
7.3.2 | shower taps with movable shower |  | 8 | pcs
7.3.3 | wash basins |  | 12 | pcs
7.3.4 | shower baths dim. 90x90 cm |  | 8 | pcs
7.3.5 | wc pans with low level flushing cistern |  | 9 | pcs
7.3.6 | urinal bowls |  | 3 | pcs
7.3.7 | water heaters 10 l |  | 6 | pcs
7.3.8 | water heaters 80 l |  | 8 | pcs
7.4 | Provision and assembly of complete shower bath, dimensions, 90x90 cm. Shower bath shall be connected with sewerage. Mount one-handed hot and cold-water tap with shower. Next to shower bath mount towel holder. |  | 6 | pcs
7. | INTERNAL WATER SUPPLY NETWORK AND SEWERAGE - TOTAL | TOTAL carried to Summary Bill No. 7
8. | FACADE WORKS
8.1 | Mounting and dismounting metal face tube scaffolds in everything according to valid regulations and measures for health and safety at work. Scaffold must be statically stable, anchored to the facility and properly earthed. Working platforms of boards shall be placed on every 2.0 m of height. Boards "on edge" shall be placed on outer side of platform. | see Tehn.spec. 6., 11.3. | 380 | m2
8.2 | Treatment of facade by rolled plastic mortar. Prior to applying, all old layers shall be removed from facade surfaces. Rub down facade surfaces with emery paper and dust off. Openings and other shall be protected with PVC foil, which shall be included into the price, but openings shall not be deducted from facade surface. | see Tehn.spec. 6., 11.3. | 240 | m2
8. | FACADE WORKS - TOTAL | TOTAL carried to Summary Bill No. 7
| SUMMARY Bill No. 7 |  |  |  |  | Amount (euro)
1. | DISMANTLING AND DEMOLITION
2. | TILING WORKS
3. | STONE MASON'S WORKS
4. | HOUSE AND WOODWORK PAINTING
5. | METALWORK
6. | JOINERY WORKS
7. | INTERNAL WATER SUPPLY NETWORK AND SEWERAGE
8. | FACADE WORKS
Bill No. 7 | BUILDING WORKS - ADMINISTRATIVE BUILDING | Total carried to Grand Summary - PART 1

## Bill No.8 WTP Electricity
Bill No.8 - WTP - ELECTRICAL PART AND CONTROL
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
GENERAL NOTE: This Bill of Quantities has included delivery, installation, testing, commissioning, trial operation and acceptance of all material and equipment as specified in particular items. The prices shall also include delivery and installation of all small unspecified material necessary for completing equipment and works, as well as for bringing into original state a part of other works damaged during the execution of installations from this project. The price of hardware equipment delivery of Supervision and Control System shall also include associated application software delivery. All material used is to be of the first class quality and in compliance with standards. All works are to be executed by expert labor, and in the whole according to technical regulations valid for the type of works concerned.
A. | PRELIMINARY WORKS
1. | Disassembly of the existing main subdistribution cabinet of pump station (machine shop), located next to +RO-CS(A), consisting of 4 sections (3 network and 1 generator), cable disconnection and disassembly of the existing equipment and its minuted delivery to the Investor. The item shall include examination and testing of the existing supply cables to motors which shall be kept. |  | 1 | set
2. | Disassembly of the existing subdistribution cabinet of ozone generator, located in ozonization building, consisting of 2 sections, cable disconnection and disassembly of the existing equipment and its minuted delivery to the Investor. The item shall include examination and testing of the existing PP00 4x185mm2 supply cable laid from NN (low voltage) supply distribution in TS (power substation) (=1NE) to ozonization building, which shall be kept. |  | 1 | set
3. | Examination of the existing installation, repair or installation of new luminaires and socket-outlets, possibly damaged due to works in pump station, filter station, sedimentation tank and ozonization building. |  | 1 | set
4. | Examination of the existing installation, repair or installation of new luminaires and socket-outlets, possibly damaged and worn-out during operation in Command -Control Centre (KKC) located in administrative building. The item shall include disassembly of the existing wall panel and control panel, preliminary works for placing newly-designed equipment of supervisory and control system (SNU). |  | 1 | set
A. | PRELIMINARY WORKS - TOTAL A | TOTAL carried to Summary Bill No. 8
B. | CABLE DISTRIBUTION
1. | Delivery and laying below specified cables in the existing conduits, in the existing and newly-designed cable racks, in floor in protective SAPA pipes, in wall on clips and in ground in trench 0.4x0.8m, with connection on both ends: | see Tehn.spec. 5.2.
1.1 | - PP00 4x95 mm2 |  | 50 | m
1.2 | - PP00 4x35 mm2 |  | 6 | m
1.3 | - PP00 4x25 mm2 |  | 170 | m
1.4 | - PP00 2x50 mm2 |  | 60 | m
1.5 | - PP00 2x16 mm2 |  | 130 | m
1.6 | - PP00-Y 5x6 mm2 |  | 90 | m
1.7 | - PP00-Y 3x6 mm2 |  | 130 | m
1.8 | - PP00 2x6 mm2 |  | 50 | m
1.9 | - PP00-Y 5x4 mm2 |  | 70 | m
1.10 | - PP00-Y 3x4 mm2 |  | 210 | m
1.11 | - PP00 2x4 mm2 |  | 140 | m
2. | Delivery and cabling in the existing conduits, in the existing and newly-designed cable racks, in floor in protective pipes, and in ground in trench, "outdoor" optical cable with minimum 8 fibers for forming "process" redundant Ethernet network 100 Mb/s in WTP "MAJDEVO", with its connection on both ends. |  | 350 | m
B. | CABLE DISTRIBUTION - TOTAL | TOTAL carried to Summary Bill No. 8
C. | DISTRIBUTION CABINETS
1. | Adaptation of leading-out terminal No. 3 in main distribution cabinet 0.4kV (=1NE+1NE2) for connection of NN power cable 2x(PP00 4x95mm2) for supplying network consumers in subdistribution cabinet +1NG in pump station. The item shall include delivery and complete installation of high performance fuses 400/400A. | see Tehn.spec. 5.1. | 1 | set
2. | Adaptation of leading-out terminal No. 3 in main distribution cabinet 0.4kV (=1NE+1NE5) for connection of NN power cable PP00 4x185mm2, for supplying ozonization consumers in subdistribution cabinet +2NG. athe item shall include delivery and installation of complete high performance fuses 400/315A. | see Tehn.spec. 5.1. | 1 | set
3. | Delivery and installation of newly designed distribution cabinet of generator supply +2NE, located next to the existing cabinet =1U in the room of diesel el. generator (DEA). Cabinet shall be made of twice-pickled sheet metal in thickness of 2mm, in protection level IP43 and shall serve for supplying newly-designed priority consumers with electric power. Cabinet dimensions shall be 600x800x250mm (WxHxD) and wall mounting is foreseen. The following equipment shall be placed in cabinet and on its door :
- feed by disconnector 125A - 1 pcs
- current instrument transformer 100/5A - 3 pcs
- amperemeter with scale 0-120 A, foreseen for connection to current instrument transformer 100/5A - 3 pcs
- complete three-pole leading out with fuse-switches 125/XX A - 10 pcs
| - other small installation material (busbars, terminals, name plates, etc.) - 1 set | see Tehn.spec. 5.1. | 1 | pcs
4. | Delivery and installation of cabinet +1NU, for distribution of battery DC supply 24VDC, made of twice-pickled sheet metal, in protection level IP43, located in pump station (machine shop). Cabinet shall be free standing with approximate dimensions of 600x1800x600mm (WxHxD). The following equipment shall be installed in the cabinet:
- three-pole disconnector, power 690V, 50Hz, 30A, with extended shaft and door pull - 1 pcs
- Modular rectifier system consisting of 3 rectifier modules, similar as Enatel RM3024 type, for parallel operation with accumulator battery. Rectifier shall be of the following characteristics: module output power : 1,7 kW rectifier output power : 5,1kW, (extendable up to 9 x 1,7kW = 15,3 kW) input voltage : 3x400V±10%, frequency : 45-65Hz, output voltage : 24VDC, fully filtrated voltage in consumers. Output characteristics IUU for charging and maintenance of encapsulated batteries, output current : 3x60A (max.), static stability of output voltage : 1%, protection against short circuit: electronic, battery current limit : electronic, protections : RST control, low input voltage, phase dropout, asimmetry by amplitude and phase 20%, fuse control, protection against a reverse-polarity battery connection, LED induction : switched on, normal operation, too high and too low output and input voltage, Relay outputs: normal rectifier operation, rectifier error, network dropout-battery operation, ... Temperature range : -10oC ... 70oC Noise level : < 50dBA - 1 set
- 19" rack for accommodation of modular rectifier (possibility to install up to 9 rectifier modules), height 3U - 1 pcs
- Supervisory measuring module, foreseen for installation in 19" rack, height 1U, similar as SM22-24 type, produced by Enatel, which carries out supervision, control and measurement of all relevant system parameters (DC voltage, rectifier current, battery current, battery temperature, fuse dropouts for 24VDC voltage distribution), with LCD alphanumeric display, SNMP protocol for remote communication and control, USB connection for local connection - 1 pcs
- Encapsulated accumulator (V.R.L.A.) batteries 24VDC, capacity 150 Ah, with terminals for front connection, life-time 12+ years (Long Life) for parallel operation with modular rectifier - 1 set
- Voltmeter 0-500V, 96x96mm, installed on cabinet door - 1 pcs
- Voltmeter selector switch (seven-position) for measurement of line and phase voltage - 1 pcs
- two-pole automatic protective switch, 24VDC, curve "C", breaking capacity 25kA, furnished with auxiliary contact for condition signalization, with rated trigger current according to power of consumers, for distribution of 24VDC battery voltage - 6 pcs
| - other equipment, various small installation and connection material, busbars, terminals, cable boots - 1 set | see Tehn.spec. 5.1. | 1 | set
5. | Delivery and installation of pump station new main subdistribution cabinet of +1NG (consisting of network and generator section) of approximate dimensions 2400x2000x600mm (WxHxD) located in machine shop next to cabinet +RO-CS(A). Subdistribution cabinet is made of twice-pickled metal sheet, in protection level IP43, and shall serve for supplying the existing and newly-designed consumers. All necessary equipment shall be installed according to single-pole diagram (Draw. No. 33) :
- feed for network section with disconnector 400A - 1 pcs
- feed for generator section with disconnector 250A - 1 pcs
- digital measuring instrument (current, voltage, power, power factor, ...) - 2 pcs
- insulation transformer 400/230V, 300 VA for forming command voltage - 2 pcs
- completely equipped motor leading-out with soft starter for supplying motor of 37kW power - 3 pcs
- completely equipped motor leading-out with frequency regulator for supplying motor of 30kW power - 2 pcs
- completely equipped leading-out for supplying compressor of 30kW power (compressor is to be moved from the existing ozonization) - 1 pcs
- completely equipped leading-out for supplying compressor of 11kW power (compressor is the existing one) - 1 pcs
- completely equipped motor leading-out with soft starter for supplying motor of 45kW power - 1 pcs
- completely equipped motor leading-out with soft starter for supplying motor of 11kW power - 1 pcs
- completely equipped motor leading-out with soft starter for supplying motor of 15kW power - 1 pcs
- completely equipped motor leading-out with soft starter for supplying motor of 7.5kW power - 2 pcs
| - other equipment, various small installation and connection material, busbars, terminals, cable boots - 1 set | see Tehn.spec. 5.1. | 1 | pcs
6. | Delivery and installation of ozonization subdistribution cabinet +2NG. Subdistribution shall be standard tested 0.4kV cabinet similar as HIMEL, PRISMA type or appropriate with the following characteristics:
- free standing, lean to wall, with doors on front side
- overall size (2x600)x2000x600mm
- protection level IP43
- access to equipment from the front
- cables leading-in from the bottom
- access to cables from the front
the following equipment shall be installed in cabinet or doors:
- Three-pole disconnector, power 400 A, 690 V, 50 Hz, making capacity 50 kA, 1s thermic short-circuit withstand current Icw=17 kA, similar as Compact NS400NA, "MG" type or appropriate - 1 pcs
- Four-pole protective switch for protection of lightening arrester 440V, 50Hz, rated current 20A, "C" curve, similar as C60L Multi 9 type or appropriate - 1 pcs
- Lightening arrester (3P+N) Imax=40kA, Up=1,2kV 8/20ms, Uc=1440V, class 2, with worn-out condition signalization, similar as PRD40r or appropriate - 1 pc
- Current transformer 300/5A, 720V, cl.0,5, 10 VA, type as TI - Multi 9 "MG" or appropriate - 3 pcs
- Digital measuring instrument, microprocessing, with display and functional keyboard, for connection to 5A and 3x400V, for measurement of electrical values (U, I, Hz, kWh, kVAh, P, Q, cos fi, phase control, ...), with communication module - 1 pcs
- Phase voltage control relay, 3x400 V, 50 Hz, with one - 1 pcs
- Door micro switch 230 V, 50 Hz - 2 pcs
Fluorescent lamp for lighting the interior of section with fluorescent luminaire 230 V, 50 Hz, length 150mm, with switch - 2 pcs
- Thermostat 230 V, 50 Hz, 6A - 1 pcs
Anti-condensation heater 220 V, 50Hz, 50W - 1 pcs
- Three-pole protective switch, 690V, 50Hz, rated current 160A, breaking capacity 25kA, fixed version, similar as Compact NSX160B type or appropriate, furnished with adjustable thermal-magnetic protective unit - 4 pcs
- Three-pole protective switch, 690V, 50Hz, rated current 125A, breaking capacity 25kA, Ics=75%Icu, fixed version, similar as Multi 9 NG125N type or appropriate, rated trigger current according to single-pole diagram - 14 pcs
- Three-pole rotary cam switch 16 A - 2 pcs
- Insuation transformer for command voltage 500 VA, 400/230 V, 50 Hz - 1 pcs
- Single-pole automatic switch, similar as C60L type or appropriate - 12 pcs
- Two-pole automatic switch, similar as C60L type or appropriate - 2 pcs
- Three-pole automatic switch, similar as C60L type or appropriate - 3 pcs
- Three-pole motor contactor 400 V, 50 Hz, 9 A, with solenoid for 230 V, 50 Hz and with 4 normally open and one normally closed contact - 7 pcs
- Three-pole motor protective switch, 10kA...100kA, with thermal overload relay and magnetic member of fixed current disconnection at short-circuit, with 2 pcs auxiliary condition signalization contact 2NO, with 1 pcs signal contact of protectieon effect, for Type 2 coordination, for 2.2kW motor power, similar as GV2-P10 type, or appropriate - 5 pcs
- Low voltage high efficiency fuse, complete base with link of the following rated current : 125/6 A - 3 pcs
- Counter of operation hours 230V, 50Hz - 2 pcs
- Amperemeter for current direct measurement with scale 0-5A - 2 pcs
- Signal lamps with LED diode and signalization test module, for installation on cabinet door, various colors - 10 pcs
- Push-button with one normally closed and one normally open contact, fi 22, for installation on cabinet door, with name plate - 10 pcs
| - various small installation and connection material, busbars, terminals, cable boots - 1 set | see Tehn.spec. 5.1. | 1 | pcs
7. | Delivery and installation of Flocculation subdistribution cabinet +3NG of approximate dimensions 600x2000x500mm (WxHxD) located in newly designed flocculation building. Subdistribution cabinet is made of twice- pickled metal sheet, in protection level IP43, and shall serve for supplying newly-designed consumers. All necessary equipment shall be installed in subdistribution cabinet according to single-pole diagram (Draw. No 1.2.):
- Feed by rotary cam switch 63A, 400V, 50Hz N/O auxiliary contact - 1 pcs
- Digital measuring instrument, microprocessing, with display and functional keyboard, for measurement of electrical values (U, I, Hz, kWh, kVAh, P, Q, cos fi, phase control, ...), with communication module - 1 pcs
- Insulation transformer 400/230V, 300 VA for forming command voltage - 1 pcs
- Disconnector switch-fuse 125/32A - 1 pcs
- Disconnector switch-fuse 125/25A - 1 pcs
- Three-pole motor protective switch, 690V, 10kA...100kA, with thermal overload relay and magnetic member of fixed current disconnection at short-circuit, with 2 pcs auxiliary condition signalization contact 2NO, with 1 pcs protection effect signal contact, for Type 2 coordination, for 1.1kW motor power, thermal relay range (2.5-4)A - 2 pcs
- Three-pole motor protective switch, 690V, 10kA...100kA, with thermal overload relay and magnetic member of fixed current disconnection at short-circuit, with 2 pcs auxiliary condition signalization contact 2NO, with 1 pcs protectieon effect signal contact, for Type 2 coordination, for 0.75kW motor power, thermal relay range (1.6-2.5)A - 2 pcs
- Three-pole motor contactor 400 V, 50 Hz, 9 A, with solenoid for 230 V, 50 Hz and with 4 normally open and one normally closed contact - 8 pcs
- Programmable logic controller for automation of "Clarification" process, with all necessary associated equipment. Rail for accommodation of PLC module, supply unit 24VDC 5A, processor module furnished with MPI port, 64 optically isolated digital inputs, 24VDC, 16 digital outputs, 4 analog inputs (4-20mA) and Ethernet communication module. The item shall also include production of appropriate PLC application software. Note : precise capacity of controller input/output signals will be defined in the Final Design - 1 set
- Operator dialogue terminal (ODT) for man-machine communication with color monitor, sensitive to touch ("touch" panel) including production of application software of the following characteristics: active monitor surface : 115.18mm x 86.38 mm (5.7") supply voltage : 24V DC mechanical protection : IP 65 (front side) interface : MPI/Profibus DP protection against unauthorized handling : yes - 1 set
- DC module, 24BDC, 6A, with 3 contacts for condition signalization, continuous supplying PLC and ODT, with VRLA battery - 1 set
- Interface relay 24VDC, with 4 changeover contacts - 10 pcs
| - various small installation and connection material, busbars, terminals, cable boots, … - 1 set | see Tehn.spec. 5.1. | 1 | pcs
8. | Delivery and installation of PA filter distribution cabinet +4NG, made of twice-pickled sheet metal, in protection level IP54, located in filter gallery. Wall mount of cabinet has been foreseen and shall have approximate dimension 700x900x250mm (WxHxD). Cabinet shall serve for 230VAC and 24 VDC voltage distribution in filter station. The following equipment shall be installed in cabinet :
- Three-pole rotary cam switch with 2 positions 0-1, 25A, 400V AC - 1 pcs
- Two-pole rotary cam switch with 2 positions 0-1, 89A, 24V DC - 1 pcs
- Single-pole automatic protective switch, 10A, 230 VAC, “C” curve - 11 pcs
- Two-pole automatic protective switch, 16A, 24 VDC, “C” curve - 11 pcs
- Signal lamp, green, 230V AC with LED diode - 3 pcs
- Signal lamp, green, 24V DC with LED diode - 1 pcs
- Single-pole automatic protective switch 2A, 230VAC, “C” curve - 3 pcs
- Two-pole automatic protective switch 2A, 24VDC, “C” curve - 1 pcs
| - Various small installation and connection material, busbars, terminals, cable boots, … - 1 set | see Tehn.spec. 5.1. | 1 | pcs
9. | Delivery and installation of sluice gate distribution cabinet +2NG.1 of approximate dimensions 600x800x250mm (WxHxD) located on exterior ozonization building wall in the immediate vicinity of sluice gates. Cabinet is made of twice-pickled sheet metal, in protection level IP65, and shall serve for supplying 3 sluice gates. All necessary equipment shall be installed in cabinet according to single-pole diagram (Draw. No. 2.3.):
- Feed by three-pole rotary cam switch 40A, 400V AC - 1 pcs
- Isolation transformer 400/230V, 300 VA for forming command voltage - 1 pc
- Three-pole motor protective switch 690V, 10kA… 100kA, with thermal overload relay and magnetic fixed current disconnection member at short-circuit, with 2 pcs auxiliary condition signalization contact 2NO, with 1 pcs protection effect signal contact, for Type 2 coordination for 3 kW motor power, range of thermal overload relay (6-10)A - 3 pcs
- Three-pole motor contactor 400 V, 50 Hz, 9 A with solenoid for 230 V, 50Hz and with 4 normally open and one normally closed contact - 6 pc
| - Various small installation and connection material, busbars, terminals, cable boots, … - 1 set | see Tehn.spec. 5.1. | 1 | pcs
C. | DISTRIBUTION CABINETS - TOTAL | TOTAL carried to Summary Bill No. 8
D. | SUPERVISORY AND CONTROL SYSTEM (SNU)
1. | Delivery, transport and installation of SCADA system equipment in Command-Control Center (KKC) for supervision, automatic control, data acquisition and visualization of complete process in WTP "MAJDEVO".
1.1. | PC computer, foreseen for continous 24-hour operation, of the following approximate characteristics:
Casing: CHIEFTEC
Supply 400W, 230V, 50Hz
Processor : Intel Pentium Core 2 Duo E6850 3.00GHz, 4MB L2 cache, 1333MHz FSB
Mother board compatible with selected processor, with 4x DDR2 slots (dual channel technology), sound, processor bus 1600MHz, furnished with RAID controller, with support for SATA II interface, 6 slots (4x PCI, 1x PCI Express x16, 1xPCI Express x1), LAN interface 10/100/1000Mbps with RJ45 connector.
Ports : - 6 x USB 2.0 port (4 back ports and 2 front ports) - 2 x serial port (V.24) - 1 x parallel port
Memory : RAM 4GB DDR2-800MHz (2 x 2GB)
Graphic card VGA 512MB GDDR3 256bit, with the possibility of simultaneous connection of 4 monitors
HDD SATA II 320 GB 7200rpm
CD ROM Drive, RW
DVD drive with burner DVD-RW
Floppy drive 3.5"
Monitor Color, TFT 19", 1280x1024 @75Hz (pcs 2)
Keyboard
Optical mouse
Windows Vista Ultimate Multi-Language (en,de,fr,it,sp)
Diagnostics and program execution monitoring software (Watchdog)
| Temperature monitoring | see Tehn.spec. 5.5. | 4 | pcs
1.2 | LASERJET laser printer, A4 paper format, 600x600dpi, USB port |  | 2 | pcs
1.3 | Color InkJet printer, A3 paper format, 1x USB port. 1x parallel port, processor 32MHz, 8MB RAM, furnished with Ethernet network card |  | 1 | pcs
1.4 | Video wall consisting of 4 pcs LCD monitors each 52” (image format 16:9), resolution 1920:1080 (FULL HD), with loudspeakers, for information graphic display from SCADA system (control supervisory system synoptics). LCDs are to have the following characteristics: USB 2.0 input 2xSCART, 3x HDMI, PC input. The item shall also include installation of appropriate video wall brackets. | see Tehn.spec. 5.5. | 1 | set
1.5 | Video wall server for simultaneous control of 4 pcs LCD monitors, with DVI and VGA outputs (expandable up to 16 LDC monitors). Server is foreseen for display of all graphic images, data, applications, presentations from internal hard disk, DVD burner or network (LAN) connections
Server configuration :
| ■ Dual 3.2 GHz processor with 2GB speed RAM and 2 x 300GB hard disk driver, 16x DVD+/- burner | see Tehn.spec. 5.5. | 1 | pcs
1.6 | Set of cables and connectors for connecting central equipment (for connecting big monitors with Video Wall Server, supply cables, rack patch cables…) | see Tehn.spec. 5.5. | 1 | set
1.7 | Laptop - portable computer for analysis and diagnostics of the following or better characteristics: processor Intel Core 2 Duo 2.1GHz, RAM 2048MB, Hard Drive 2x160GB, DVDRW Super Multi, communication: 56K, GigaLAN, WLAN 802.11b, WLAN 802.11g, Bluetooth, 17” monitor, OS Windows Vista | see Tehn.spec. 5.5. | 1 | pcs
1.8 | CABINET +1NY
Delivery and installation of communication cabinet +1NY in a room behind command-control room located in administrative building, made of twice-pickled sheet metal, protected with primer and finish paint. Cabinet is free standing of approximate dimensions 600x200x800mm (WxHxD), with air grills on cabinet sides diagonally positioned in cabinet bottom and upper part and transparent door, mechanically protected in protection level IP43, with lock and key. Cabinet shall be furnished with vertical support rails for forming 19” rack system. The following equipment shall be installed in the cabinet:
1.8.1. | Uninterruptible power supply system (UPS), for mounting in 19” rack (3U) for supply of Working Stations (2 pcs), Engineer Station and network equipment, with the following characteristics: - intended for on-line mode, - supply voltage 230V, 50Hz, - output voltage 230V±1%, 50Hz/24V DC, - power 4.0kVA, - exterior battery package (19)” for conjugated operation with uninterruptible power supply device. Battery capacity, taking into account inverter minimum input DC voltage, must be sufficient to provide UPS operation for a minimum of 30 minutes at load 4kVA, taking into account inverter losses. - Ethernet connection for connecting to LAN network - appropriate software
| Ambient temperature: 0 to + 450C Relative ambient humidity: 0 to 95% without condensation. UPS shall be with condition light signalization (overload, device on batteries, discharged batteries) and possibility of basic status and alarm transmission via dead contacts. In addition to equipment delivery, it has been foreseen that the item shall include complete connection and commissioning and customer's training.. | see Tehn.spec. 5.5. | 1 | set
1.8.2 | Gigabit Ethernet switch, 24-port, Layer 3, QoS, PoE controllable, intended for installation in 19" rack 24x10/100/1000Mbps RJ45 ports, supply 230V AC. | see Tehn.spec. 5.5. | 1 | pcs
1.8.3 | Safety modular VPN Router, with 2x10/100TX WAN ports, 5x 10/100TX LAN ports, 2x PIC slots and 1x Async console. | see Tehn.spec. 5.5. | 1 | pcs
1.8.4 | GPS time synchronization , with external GPS antenna for satellite signal reception. Device shall be connected to "OFFICE" LAN network via integrated Ethernet interface. Complete delivery, installation and connection. | see Tehn.spec. 5.5. | 1 | set
1.8.5 | Other necessary active and passive equipment (switches, routers, patch panels, via-cables, connectos, etc.) for correct SCADA system connection to "office" network and "process" network. | see Tehn.spec. 5.5. | 1 | sum
1.8 | TOTAL CABINET +1NY :
1.9 | SCADA application software, multi-language support. Additional options included : client/server configuration, redundant operation, Web browser, user archives, storage, open communication via OPC. SCADA application shall include three operator stations and one engineer station. The item shall also include application software for automatic supervision and control and SCADA system data acquisition, data base configuration, monitor displays, alarm and other functions. | see Tehn.spec. 5.5. | 1 | set
1.10 | SCADA system testing and commissioning | see Tehn.spec. 5.5. | 1 | pcs
1.11 | Preparation of Operation and maintenance manual and personnel training. Training shall be carried out in situ for plant operators and technical personnel. | see Tehn.spec. 5.5. | 1 | pcs
1 | Total Item 1: SCADA system: 1.1+1.2+1.3+1.4+1.5+1.6+1.7+1.8+1.9+1.10+1.11 | Sub-total carried to Summary D.
2. | PA FILTERS CONTROL CABINETS
2.1. | Delivery and installation of PA filters Control cabinets (+1WF...+8WF), located in pipe gallery, made of twice-pickled sheet metal, protected with primer and finish pain coating. CabInets are intended for wall mounting and shall be of approximate dimensions 800x600x300mm (WxHxD), mechanically protected in protection level IP54, with lock and key. Valve island and PLC with electric periphery shall be accommodated in cabinets.
Specification contains only electrical equipment built into control cabinet, while pneumatic equipment has been specified in mechanical part of project.
The following electrical equipment shall be installed in the cabinet :
Rotary cam switch with 2 positions 0-1, 25A, 230VAC installed on outer cabinet side - 1 pcs
Stabilized supply unit, input voltage 230V AC, rated output voltage 24VDC, 5A, with short-circuit protection, LEDfunction indication - 1 pcs
DC UPS module, 24VDC, 6A, with 3 condition signalization contacts, for continuous PLC and ODT supply, with appropriate VRLA battery - 1 set
Two-pole selector switch, 10A, 230VAC, with locking possibility - 1 pcs
Compact programmable logic controller (PLC) for process control over one filter field, similar as SIMATIC S7-300 type , CPU 313C-2DP, or appropriate. Controller shall consist of processor unit with MPI interface and integrated 24 digital inputs/16 digital outputs, 4 analog inputs, 2 analog outputs, 1 PT100 input, 4 fast counters (60kHz), integrated DP interface, integrated 24V DC supply, 64kByte working memory, 40-pin front connector and foreseen place for accommodation of micro memory card. The item shall also include production of application software for one PA filter - 1 pcs
Communication processor CP 343-1, for connection such a SIMATIC S7-300 type or appropriate to Industrial Ethernet 100Mbps via RJ-45 port - 1 pcs
Note : The price of programmable controller delivery shall also production of application software for filter field.
Measurement transmitters with standardized current output (4-20)mA, supply voltage 24VDC - 1 set
Fluorescent lamp for lighting the interior of cabinet with fluorescent luminaire 30W, 230V AC, with switch 230V, 10A and socket with protective earthing contact 10A - 1 pc
Anti-condensation heater 220 V, 50Hz, 50W - 1 pcs
Thermostat with adjustment range 0...60°C, with a pair of output contacts 6A, 230VAC - 1 pcs
Door micro switch 6A, 230VAC - 1 pcs
| Other unspecified material : automatic fuses, auxiliary relays, signal lamps, copper rails, insulators, line-up terminals, conductors, name plates, hardware, lead-ins, wiring channels, etc. - 1 set | see Tehn.spec. 5.5. | 8 | pcs
2. | PA FILTERS CONTROL CABINETS -TOTAL | Sub-total carried to Summary D.
3. | OPERATOR DIALOGUE TERMINALS (ODT)
3.1. | Operator dialogue terminals (ODT) for supervision and control of filters, with associated application software, such as TP177B type or appropriate, installed in special console with ergonomic slope. ODT with console shall be installed in front of each filter section.
ODT shall be of the following characteristics :
- Display : Color LCD STN display (256 colors) with touch screen, active display surface : 115.18mm x 86.38 mm (5.7")
- setting commands : through Touch screen
- Memory: 2 MB
- Supply voltage : 24V DC
- Interface : MPI-/PROFIBUS DP, 1xRS232 and USB
- Temperature range : 0....+50oC
- Mechanical protection level : IP 65 (front side)
- Total dimensions : 212x156mm (WxH)
| - With protection against unauthorized handling | see Tehn.spec. 5.5. | 8 | pcs
3. | Total Item 3 : OPERATOR DIALOGUE TERMINALS | Sub-total carried to Summary D.
4. | TELECOMMUNICATION CABINET
4.1. | Delivery and installation of telecommunication 19" rack cabinet, at suitable place in filter station, for Industrial Ethernet Switch and other necessary equipment for forming "process" optical network at WTP "MAJDEVO". |  | 1 | set
4. | Total Item 4 : TELECOMMUNICATION CABINET | Sub-total carried to Summary D.
5. | INTERFACE CABINET
Delivery and installation of interface cabinet (=W03.0+1NW, =W11.0+2NW, =W01.0+3NW) for automation of part of technological process. Cabinet is made of twice-pickled sheet metal, protected with primer and finish paint coating. Cabinet is free standing, of approximate dimensions 800x2000x600mm (WxHxD), mechanically protected in protection level IP43, with lock and key. Cabinet shall be delivered completely connected and tested. The following equipment shall be installed into cabinet :
Feed by rotary cam switch 25A, 400V, 50Hz with one N/O auxiliary contact - 1 pcs
Cabinet shall be delivered completely connected and tested. The following equipment shall be installed into cabinet : Feed by rotary cam switch 25A, 400V, 50Hz with one N/O auxiliary contact - 1 pcs Programmable logic controller (PLC), with all necessry associated equipment and including production of application software. Rail for PLC module accommodation, supply unit 230VAC/24VDC 5A, processor module furnished with MPI port, 144 optically insulated digital inputs 24VDC, 32 digital outputs, 16 analog inputs (420mA) and Ethernet communication module - 1 set Note : precise capacity of input/output signals of each individual controller will be specified in the Final Design.
Operator dialogue terminal (ODT) for man-machine communication with color monitor, touch panel with associated application software of the following characteristics: monitor active surface : 115.18mm x 86.38 mm (5.7") supply voltage : 24V DC mechanical protection : IP 65 (front side) interface : MPI/Profibus DP protection against unauthorized handling - 1 pcs
Industrial Ethernet switch 10/100Nbs, controllable, for PLC connection to “process” network, complete with necessary communication cables and connectors - 1 set
DC UPS module, 24 VDC, 6A, with 3 condition signalization contacts, for continuous PLC and ODT supply, with appropriate VRLA battery - 1 set
Interface relay 24VDC, with 4 changeover contact - 25 pcs
Single-pole automatic protective switch, 440V, 6A - 10 pcs
Door micro switch 230 V, 50 Hz - 1 pc
Fluorescent lamp for lighting the interior of sections with fluorescent lamp 230 V, 50Hz, length 150 mm, with switch - 1 pcs
Thermostat 230 V, 50Hz, 6A - 1 pcs
Anti-condensation heater 230 V, 50 Hz, 100W - 1 pcs
| Other equipment, various small installation and connection material, busbars, terminals, cable boots, … - 1 set | see Tehn.spec. 5.5. | 3 | set
5. | Total Item 5 : INTERFACE CABINET | Sub-total carried to Summary D.
D | SUMMARY D. SUPERVISORY AND CONTROL SYSTEM (SNU)
Amount (euro)
1. | SCADA SYSTEM EQUIPMENT
2. | PA FILTERS CONTROL CABINETS
3. | OPERATOR DIALOGUE TERMINALS (ODT)
4. | TELECOMMUNICATION CABINET
5. | INTERFACE CABINET
D. | SUPERVISORY AND CONTROL SYSTEM (SNU) | TOTAL carried to Summary Bill No. 8
E. | TECHNOLOGICAL VIDEO SUPERVISION
1. | Disassembly of the existing equipment for video supervision and its minuted delivery to the Investor. | see Tehn.spec. 5.7. | 1 | sum
2. | Video supervision server (video encoders), with Ethernet port for image transmission in filter station, sedimentation tanks, ozonization building… Due to increased humidity in facility, video server should be in protection suitable to working conditions of 80% humidity. Supply 230 V, 50 Hz. Provision, delivery and installation. | see Tehn.spec. 5.7. | 1 | pcs
3. | Color supervision camera, intended for operation in higher humidity conditions, with connection cable and adapter for AC voltage 230 V, 50 Hz supply. Provision, delivery and installation. Connection to video server | see Tehn.spec. 5.7. | 7 | pcs
4. | Installation, connection (of all elements and systems) and programming the central video supervision. | see Tehn.spec. 5.7. | 1 | set
E. | TECHNOLOGICAL VIDEO SUPERVISION - TOTAL | TOTAL carried to Summary Bill No. 8
F. | CABLES AND CABLE ACCESSORIES FOR TECHNOLOGICAL CONSUMERS
1. | Delivery and laying power cables, from newly-designed subdistribution cabinets to newly- designed technological consumers with connection on both ends, of the following types and sections :
1.1 | - PP00 4x50 mm2 |  | 60 | m
1.2 | - PP00 4x25 mm2 |  | 130 | m
1.3 | - PP00-Y 1x25 mm2 |  | 130 | m
1.4 | - PP00-Y 1x35 mm2 |  | 60 | m
1.5 | - Braided power cable with copper cores of type Topflex-EMV-UV 2YSLCYK-J 4G35 |  | 60 | m
1.6 | - PP00-Y 5x10 mm2 |  | 40 | m
1.7 | - PP00-Y 4x10 mm2 |  | 70 | m
1.8 | - PP00-Y 5x6 mm2 |  | 50 | m
1.9 | - PP00-Y 4x6 mm2 |  | 140 | m
1.10 | - PP00-Y 5x4 mm2 |  | 70 | m
1.11 | - PP00-Y 3x4 mm2 |  | 60 | m
1.12 | - PP00-Y 5x2.5 mm2 |  | 150 | m
1.13 | - PP00-Y 4x2.5 mm2 |  | 280 | m
1.14 | - PP00-Y 3x2.5 mm2 |  | 100 | m
2. | Delivery and laying signal and communication cables, of the following types, number of cores and cross sections with connection on both ends..
2.1 | - IY(St)Y 6x2x0.8 |  | 100 | m
2.2 | - LiYCY 2x0.75mm2 |  | 200 | m
2.3 | - LiYCY 7x0.75mm2 |  | 60 | m
2.4 | - LiYCY 5x2x0.75mm2 |  | 60 | m
2.5 | - Profibus cable |  | 60 | m
2.6 | - STP 4x2x0.5mm, Cat. 6 |  | 180 | m
3. | Provision, material delivery and installation of perforated (PNK) and ladder (RNK) cable trays with necessary accessories. Complete per m'.
3.1 | - PNK 100 |  | 120 | m
3.2 | - PNK 200 |  | 120 | m
3.3 | - RNK 200 |  | 20 | m
F. | CABLES AND CABLE ACCESSORIES FOR TECHNOLOGICAL CONSUMERS - TOTAL | TOTAL carried to Summary Bill No. 8
G. | PROCESSING EQUIPMENT IN PLANT
1. | Probes for direct measuring water level in filters complete with cables, distribution box and bracket.. Probe characteristics shall be: - cable type : PVC - cable length : 5 m - number of probes: 3 (min, max, GND) - level of mechanical protection : IP68 |  | 8 | set
2. | Probe for continuous measuring the level in filter pools, based on hydrostatic pressure principle, similar as NIVOPRES NPK-2 or appropriate, complete with distribution box and bracket. |  | 8 | set
Note : Flowmeter specifications and prices are included in Hydro-Mechanical part of project.
G. | PROCESSING EQUIPMENT IN PLANT - TOTAL G. : | TOTAL carried to Summary Bill No. 8
H. | GENERAL INSTALLATIONS IN NEWLY-DESIGNED FACILITIES
1. | FLOCCULATION (“CLARIFICATION”) FACILITY
1.1. | Delivery, installation and connection of general-purpose distribution board +3NG.1, foreseen for wall mounting, placed in flocculation building in room for preparation of chemicals. Board shall be made of twice-pickled metal sheet in thickness of 2 mm, with door and key, painted according to the Investor’s wish. Board dimensions to be determined according to the equipment built in. The following equipment shall be installed in board:
-Three-pole rotary cam switch 4G-40-10U, rated current 40 A, 400V, 50Hz - pcs
- single-pole automatic fuse MC32 type U:
rated current 16 A - 1 pcs
rated current 10 A - 9 pcs
rated current 6A - 1 pcs
rated current 2A - 3 pcs
- two-pole automatic fuse MC32 type U:
rated current 10 A - 1 pcs
- three-pole automatic fuse MC32 type U:
rated current 16 A - 1 pcs
- four-pole protective switch for protection of lightening arrester 400V, 50Hz, rated current 20A, “C” curve - 1 pcs
- lightening arrester Imax=15kA, 8/20ms, Uc=440V, class 2, with worn-out condition signalization - 4 pcs
- reduced voltage transformer 230/24VAC, 300VA, 50Hz - 1 pcs
-Single-phase socket-outlet 16A, 400V, 50Hz in cabinet - 1 pcs
-Three-phase socket-outlet 16A, 400V, 50Hz in cabinet - 1 pcs
-Single-phase socket-outlet for reduced voltage 10A, 24VAC for installation in cabinet, 2P - 1 pcs
- signal lamp with green cap and LED diode 1.2W, 240V, for voltage presence signalization - 3 pcs
- other small installation material (busbars, terminals, name plates, etc.) - 1 set
| All completely connected and tested | see Tehn.spec. 5.3. | 1 | set
1.2. | Delivery and wall and ceiling mount of lamps by appropriate installation accessories, complete with bulbs and connection, as follows:
1.2.1 | - Lamp similar as BFN 236 “TITAN”-BUCK type with fluorescent bulbs of quality 36/840 2x36W, IP 65 | see Tehn.spec. 5.3. | 34 | pcs
1.2.2 | - Industrial wall mount metal-halogen lamp, similar as EKO 3 “Minel Schreder” type with metal-halogen bulb 150W, 230V, intended for outdoor installation, installed above entrance door | see Tehn.spec. 5.3. | 5 | pcs
1.3. | Delivery and installation of installing material for wall mount (switches, distribution boxes):
| - Delivery and installation of series switch OG, 6A, 230V, 50Hz | see Tehn.spec. 5.3. | 5 | pcs
1.4. | Delivery of material and fabrication of lighting installation with cables PPOO-Y2,3 and 4X1.5mm2, average length 12m. Cables shall be run in racks, visibly on wall with clips, in SAPA protective pipes. | see Tehn.spec. 5.3. | 39 | pcs
1.5. | Fabrication of foundation FeZn earthing tape 25x4mm JUS N.B4 901.Tape shall be laid in foundation above the first concrete layer and welded to foundation reinforcement on every 2 meters. The item shall include delivery and installation of tape, connection material and its connection by welding to facility foundation | see Tehn.spec. 5.3. | 150 | m
1.6. | Delivery and installation of FeZn tape 25x4mm from foundation earthing tape to GSIP and connection on both ends. | see Tehn.spec. 5.3. | 1 | m.
1.7. | Delivery and installation of busbar for potential equalization (GSIP) in standard box next to the cabinet +3NG. | see Tehn.spec. 5.3. | 1 | pcs
1.8. | Delivery and laying cable PPOO-Y 2x26mm2 1kV, with connection on both ends. Cable shall be laid from metal earth terminal to GSIP. | see Tehn.spec. 5.3. | 50 | m.
1.9. | Cross run clamp for connecting and branching earthing tape and wires JUS N.B4936. | see Tehn.spec. 5.3. | 25 | pcs
1.10. | Delivery and installation of FeZn tape 25x4mm as earthing lead-in from test joint with gutter clip to earthing tape with connection. | see Tehn.spec. 5.3. | 14 | m.
1.11. | Delivery and installation on facility roof of lightning arrester made of FeZn tape 25x4 mm. The item shall also include tape brackets on roof. | see Tehn.spec. 5.3. | 70 | m.
1.12. | Delivery and installation of FeZn tape 25x4 mm on the building wall in appropriate supports | see Tehn.spec. 5.3. | 20 | m.
1.13. | Delivery and installation of test joints in test joint box for test joint JUS N.B4.912 on wall, at height of 1.6 m from ground, with installation of steel “L bar” | see Tehn.spec. 5.3. | 6 | pcs
1.14. | Delivery and installation of gutter clip according to gutter type built-in. | see Tehn.spec. 5.3. | 8 | pcs
1.15. | Delivery and installation of arrester on gutter, as well as its connection to the installed FeZn tape 25x4mm. | see Tehn.spec. 5.3. | 6 | pcs
1. | FLOCCULATION FACILITY - TOTAL | Sub-total carried to Summary H.
2. | LIQUID OXYGEN GASIFICATION STATION
2.1. | Cabinet +NG.2
Delivery and mounting metal cabinet made of twice-pickled sheet metal in thickness of 1.5 mm with doors in the front on fence metal post. Cabinet shall be painted with primer and baking finish paint.
| A four-pole three-phase socket-outlet, type PROP-IV-63A shall be installed in the cabinet. | see Tehn.spec. 5.4. | 1 | pcs
2.2. | 2.2 Protective earthing
2.2.1 | Fabrication of FeZn earthing tape 25 x4 mm laid in tank concrete foundation and partially welded to foundation reinforcement. Foundation reinforcement shall also be mutually welded with 20 cm weld overlap. Lead-outs shall be left from this foundation earthing tape for connection to outdoor lighting and ozonization facility earthing tape. | see Tehn.spec. 5.4. | 30 | m.
2.2.2 | Delivery and installation of potential equalization busbar (SIP) and FeZn tape 25 x 4 mm from foundation earthing tape to SIP. Pile shall be installed in box mounted on the same post as cabinet +2NG.2. | see Tehn.spec. 5.4. | 1 | pcs
2.2.3 | Delivery of material and connection of all metal mass (metal fence, gates, metal pipes, etc.) mutually and to earthing tape by Cu cable 16 mm2. | see Tehn.spec. 5.4. | 25 | pcs
2.2.4 | Examination of all galvanic connections. |  | 1 | sum
2.2.5 | Measurement of earthing and issuance of certificate of compliance. |  | 1 | sum
2. | LIQUID OXYGEN GASIFICATION STATION - TOTAL | Sub-total carried to Summary H.
H | SUMMARY D. GENERAL INSTALLATION OF NEWLY-DESIGNED FACILITIES
Amount (euro)
1. | FLOCCULATION (“CLARIFICATION”) FACILITY
2. | LIQUID OXYGEN GASIFICATION STATION
H. | GENERAL INSTALLATION OF NEWLY-DESIGNED FACILITIES | TOTAL carried to Summary Bill No. 8
I. | FINAL WORKS
1. | Measurements in installation :
- Measurement of insulation resistance, loop resistance, checking conditions of protection against electric shock
- Measurement of earthing resistance of earthing tape
| - Measurement of galvanic connection in potential equalization | see Tehn.spec. 5.6. | 1 | sum
2. | Drawing into changes arisen during the execution of works and development of the As-Built Design | see Tehn.spec. 5.6. | 1 | sum
3. | Commissioning all installations and issuance of guarantees for executed works for all specified items with issuance of necessary certificates of compliance. | see Tehn.spec. 5.6. | 1 | sum
I. | FINAL WORKS - TOTAL | TOTAL carried to Summary Bill No. 8
| SUMMARY Bill No. 8 |  |  |  |  | Amount (euro)
A. | PRELIMINARY WORKS
B. | CABLE DISTRIBUTION
C. | DISTRIBUTION CABINETS
D. | SUPERVISORY AND CONTROL SYSTEM (SNU)
E. | TECHNOLOGICAL VIDEO SUPERVISION
F. | CABLES AND CABLE ACCESSORIES FOR TECHNOLOGICAL CONSUMERS
G. | PROCESSING EQUIPMENT IN PLANT
H. | GENERAL INSTALLATIONS IN NEWLY-DESIGNED FACILITIES
I. | FINAL WORKS
Bill No. 8 | ELECTRICAL PART AND CONTROL | Total carried to Grand Summary - PART 1

## Bill No. 9 - CCMS Electricity
Bill No. 9 - CENTRALISED CONTROL AND MONITORING SYSTEM FOR THE REGIONAL WATER SUPPLY SYSTEM CELIJE
Item | Description | Close specification | Unit | Qty. | Rate (Euro) | Amount (Euro)
See Technical Specification - Vol 3. - Part 2
A | SUBSYSTEM „REGIONAL SYSTEM“
I | COMMAND AND CONTROL CENTRES
1 | CCC1 - LIPOVAC
1.1 | Construction and furbishing of the command and control centre CCC1 Lipovac for the regional water supply system |  | set | 1
o premises construction
o furbishing of the centre
In the scope of the command building construction investment.
1.2 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Central access unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used IP V4, UDP, TCP , IC MP, Telnet, HTTP , FTP , SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Wind resistance 190 km/hr
Temperature range: -40°C to +55°C
Radio-device, ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Point-to-point unit pcs 2
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip. Allowed passive reflector to be added
Antenna Beam Width 3 dB internal antenna beam width 60deg. Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used: IP V4, UDP, TCP, IC MP, Telnet, HTTP, FTP, SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Temperature range: -40°C to +55°C
Point -to-Point devices, can be with passive reflectors, with minimal requirements:
Signalling Rate: min.10 Mbps
Aggregate Throughput: min.7.5 Mbps
Typical LoS Range 56 km with passive reflector
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 2
Base station control and management module with functions:
radio-devices management, GPS synchronization min.8 access ports Managed Switch with a Network manager using Simple Network Management Protocol (SNMP).
Module to allow direct connection and synchronization of point-to-point device Power supply - Power over Ethernet, 24VDC @ 3.5 AMP Typical (4.0 AMP Max)
Environmental -40°C to +55°C /
Enclosure to be suitable for outdoor use, IP56, with water sealed cable entries. To be delivered with mounting clamps for tubular mast pcs 1
EU power cord pcs 1
Antenna mast, steel single-tube, zinc-plated, diameter min. 100mm, three section, h=15m, with mounting clamp, earthing gland and shrouds. pcs 1
Power supply unit (PSU) for base station control module 90-240VAC/ 24VDC, 3A continuous duty, with Ethernet by pass pcs 2
Ethernet Surge Suppressor , for outdoor installation pcs 1
FTP cable cat.5e, patch, 30m pcs 4
Radio-device and control module outdoor installation pcs 4
Set-up and configuration of radio-device and control module pcs 4
Unspecified consumables pcs 1
1.3 | LAN Ethernet 10/100 BaseT installation, including the following: Ethernet Switch L2, UTP cable 150m, surge protection devices, wiring ducts |  | set | 1
Active and passive LAN equipment
16-ports 10/100/1000 Mbps Gigabit Switch, 1U / 19", for rack mounting, TLSG1016
Rack cabinet 19"/6HE, with a window door and a twist lock
Cable glands and clips
Patch panel 24,CAT6 and connection cables
UTP (Unshielded Twisted Pair) cable installation inside the command building, including the centre itself, the maintenance department manager office and the system administrator office.
1.4 | The main server and six monitoring PC stations, each intended for one of six water supply subsystems, all connected to the LAN. The computers will have the following characteristics: |  | pcs | 7
KC C2D8400,2GB,2x500 GB
LGA775, P35+ICH9, FSB 1333/1066/800, PCI-E X16,
4xDual Channel DDRII, 3PCI, 3PCI-E, SB, PCI-E
GiGaBit Lan, 6xSATAII, 1xPATA, 1xPATA, RAID
1,0,5,10, Virtual Dual BIOS, ATX, RoHSGA-EP43-DS3LR
LGA775 E8200
DDR2- 800 MHz, 1GB PC 6400
500GB,7200rpm, SATA II, 16MBWD5000A AKS WD
DVD RW 20x speed, black, bulk, SecureDisc GSAH55N RBB LG
ATI VGA HD 2400 PRO 256M GDDR3 PCI-E DUAL DVI-IHD 2900PRO 512M PALIT
Mini Tower ATX 450 W, USB, Audio, Black TLA 481
Mouse, PS2 Optical
Keyboard PS2
Windows XP Professional OEM CD
1.5 | Monitoring stations' monitors |  | pcs | 6
Panel Viewable area 22" Wide; Brightness 300 cd/m²
Contrast Ratio 1000:1 ; Viewing Angle (H/V) 170˚/160˚ (CR>10)
Response Time (ms) 5 - ; Maximum Resolution 1680 x 1050
Colour Supported 16.7 Mil.
Signal Input Input Video Signal Analog RGB
Sync Type Separate H/V, Composite, SOG
Input Connectors 15pin D-SUB
Plug & Play DDC 2B
USB powered hub option
Mac compatibility Yes
Power On Mode 46 Watts (Max.)
DPMS Mode <1 Watt
Type Built-in
Multimedia Speakers 2 W x 2
Wall-Mount VESA 10
1.6 | The main server monitor, 17", TFT monitor |  | pcs | 1
Panel Viewable area 17" Wide; Brightness 300 cd/m² Contrast Ratio 1000:1 ; Viewing Angle (H/V) 170˚/160˚ (CR>10) Response Time (ms) 5 - ; Maximum Resolution 1680 x 1050 Colour Supported 16.7 Mil. Signal Input Input Video Signal Analog RGB Sync Type Separate H/V, Composite, SOG Input Connectors 15pin D-SUB Plug & Play DDC 2B USB powered hub option Mac compatibility Yes Power On Mode 46 Watts (Max.) DPMS Mode <1 Watt Type Built-in Multimedia Speakers 2 W x 2 Wall-Mount VESA 10
1.7 | Delivery, installation and commissioning of UPS devices |  | pcs | 7
Output Power Capacity 980 Watts / 1500 VA
Max Configurable Power 980 Watts / 1500 VA
Nominal Output Voltage 230V
Output Voltage Note Configurable for 220 : 240 V
Output Voltage Distortion Less than 5% at full load
Output Frequency (sync to mains) 47 - 53 Hz for 50 Hz nominal,
Crest Factor up to 5 : 1
Waveform Type Sine wave
Output Connections IEC 320 C13
Nominal Input Voltage 230V
Input Frequency 50/60 Hz +/- 3 Hz (auto sensing)
Input voltage range for main operations 160 - 286V
Input voltage adjustable range for mains operation 151 - 302V
Battery Type Maintenance-free sealed Lead-Acid battery
Typical recharge time 3 hour(s)
Typical Backup Timeat Half Load 23.9 minutes (490 Watts)
Typical Backup Timeat Full Load 6.7 minutes (980 Watts)
Interface Port(s) DB-9 RS-232,SmartSlot,USB
Available SmartSlot™ Interface Quantity
Control panel LED status display with load and battery bar-graphs and On Line : On Battery : Replace Battery : and Overload Indicators Audible Alarm
Alarm when on battery : distinctive low battery alarm : configurable delays
Surge energy rating 480 Joules
Filtering Full time multi-pole noise filtering
1.8 | Programmable Logic Controller Master PLC1.1, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025
CPU: CJ1M-CPU13 -NL
Ethernet module: CJ1W-ETN21
1.9 | The application software for the Master PLC1.1, providing: |  | set | 1
a. client/server communication with all communication centres and the main server,
b. concentration of all regional system real-time data in a main data storage memory area,
c. control loop closing for all pairs of hydraulically coupled objects, in order to provide remote automatic operation mode,
d. analysis and verification of command messages obtained from the main server,
e. diagnostic functions for the logical WLL with command centres and Master itself.
1.10 | Supply, delivery, installation and commissioning of the ROMTK distribution cabinet, dimensions WxHxD 600x550x250, containing: |  | set | 1
the Master PLC-1.1,
parts of network equipment,
UPS Supply SLAC24, with the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit, status outputs and indicator system. Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max Thermal protection: yes 24V output (mains 220V): Voltage: 23.2V + / - 2% Current: limited to 3A Thermal protection: yes Output 24V (battery power): Voltage: Battery voltage - 0.25V Current: limited to 5A Thermal protection: no 12V output: Voltage: 13.2V + / - 2% Current: limited to 3A Thermal protection: yes Status Output: POWER OK: Threshold 23V - signals the presence of mains power ACCU OK: Threshod 22.2V/22V - signals that battery is not empty BACKUP: Threshold 20V - The device moved the power from batteries CHARGING: Threshold 0.8A - Charging current greater than 0.8A Display system - alphanumeric display to display measured values: "Iout [A]” ,output current , output 24V "Vout [V]”, output voltage, output 24V "Vacc: [V]”, battery voltage "Ichg: [A]", charging current "Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
Complete
1.11 | Laser printer A4 |  | pcs | 1
1 | CCC1 LIPOVAC - TOTAL | Sub-total carried to Summary I
2 | CCC2 - DIREKCIJA
2.1 | Establishing of the command and control centre CCC2 Direkcija at the new premises, within the main management building Direkcija |  | set | 1
o premises construction
o furbishing of the centre
2.2 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Central access unit pcs 2
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used IP V4, UDP, TCP , IC MP, Telnet, HTTP , FTP , SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Software Upgrade remote downloaded in FLASH over RF link
Wind resistance 190 km/hr
Temperature range: -40°C to +55°C
Dimensions (basic enclosure) max.29.9 cm H x 8.6 cm W x 8.6 cm D
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply:24VDC, power over Ethernet
Point-to-point unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip. Allowed passive reflector to be added
Antenna Beam Width 3 dB internal antenna beam width 60deg. Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used IP V4, UDP, TCP , IC MP, Telnet, HTTP , FTP , SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Software Upgrade remote downloaded in FLASH over RF link
Wind resistance 190 km/hr
Temperature range:-40°C to +55°C
Dimensions (basic enclosure) max. 29.9 cm H x 8.6 cm W x 8.6 cm D
Point -to-Point devices, can be with passive reflectors, and minimal requirements need to be met:
Signalling Rate: min.10 Mbps
Aggregate Throughput: min.7.5 Mbps
Typical LoS Range 56 km with passive reflector
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 1
Base station control and management module with functions:
radio-devices management, GPS synchronisation
min. 8 access ports Managed Switch with a Network manager using Simple Network
Management Protocol (SNMP).
Module to allow direct connection and synchronization of point-to-point device Power supply - Power over Ethernet, 24VDC @ 3.5 AMP Typical (4.0 AMP Max)
Environmental -40°C to +55°C /
Dimensions of enclosure: max. 30 x 25 x 7,5 cm
Enclosure to be suitable for outdoor use, IP56, with water sealed cable entries. To be delivered with mounting clamps for tubular mast pcs 1
EU power cord pcs 1
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Power supply unit (PSU) for base station control module 90-240VAC/ 24VDC, 3A continuous duty, with Ethernet by pass pcs 2
Ethernet Surge Suppressor , for outdoor installation pcs 1
FTP cable cat.5e, patch, 30m pcs 4
Radio-device and control module outdoor installation pcs 4
Set-up and configuration of radio-device and control module pcs 4
Unspecified consumables pcs 1
2.3 | Expanding the existing LAN to suit the CCMS needs |  | set | 1
UPT cable installation; expanding, connecting and testing of the LAN, all within the main management building Direkcija
2.4 | Supply, delivery and installation of the monitoring station, a PC computer of the following characteristics: |  | pcs | 1
KC C2D8400,2GB,2x500 GB
LGA775, P35+ICH9, FSB 1333/1066/800, PCI-E X16,
4xDual Channel DDRII, 3PCI, 3PCI-E, SB, PCI-E
GiGaBit Lan, 6xSATAII, 1xPATA, 1xPATA, RAID
1,0,5,10, Virtual Dual BIOS, ATX, RoHSGA-EP43-DS3LR
LGA775 E8200 Intel
DDR2- 800 MHz, 1GB PC 6400
500GB,7200rpm, SATA II, 16MBWD5000A AKS WD
DVD RW 20x speed, black, bulk, SecureDisc GSAH55N RBB LG
ATI VGA HD 2400 PRO 256M GDDR3 PCI-E DUAL DVI-IHD 2900PRO 512M PALIT
Mini Tower ATX 450 W, USB, Audio, Black TLA 481
Mouse, PS2 Optical S90
Keyboard PS2,black Deluxe 250
Windows XP Professional OEM CD
2.5 | A monitor for the monitoring PC station |  | pcs | 1
Panel Viewable area 22" Wide; Brightness 300 cd/m²
Contrast Ratio 1000:1 ; Viewing Angle (H/V) 170˚/160˚ (CR>10)
Response Time (ms) 5 - ; Maximum Resolution 1680 x 1050
Colour Supported 16.7 Mil.
Signal Input Input Video Signal Analog RGB
Sync Type Separate H/V, Composite, SOG
Input Connectors 15pin D-SUB
Plug & Play DDC 2B
USB powered hub option
Mac compatibility Yes
Power On Mode 46 Watts (Max.)
DPMS Mode <1 Watt
Type Built-in
Multimedia Speakers 2 W x 2
Wall-Mount VESA 10
2.6 | Dismantling of the existing radio-communication and controller equipment |  | set | 1
Dismantle the radio-communication cabinet, aerial system and the existing cabinet with the Master PLC-1.1.
2.7 | Delivery, installation and commissioning of an UPS for the monitoring station |  | pcs | 1
Output Power Capacity 980 Watts / 1500 VA
Max Configurable Power 980 Watts / 1500 VA
Nominal Output Voltage 230V
Output Voltage Note Configurable for 220 : 240 V
Output Voltage Distortion Less than 5% at full load
Output Frequency (sync to mains) 47 - 53 Hz for 50 Hz nominal,
Crest Factor up to 5 : 1
Waveform Type Sine wave
Output Connections IEC 320 C13
Nominal Input Voltage 230V
Input Frequency 50/60 Hz +/- 3 Hz (auto sensing)
Input voltage range for main operations 160 - 286V
Input voltage adjustable range for mains operation 151 - 302V
Battery Type Maintenance-free sealed Lead-Acid battery
Typical recharge time 3 hour(s)
Typical Backup Timeat Half Load 23.9 minutes (490 Watts)
Typical Backup Timeat Full Load 6.7 minutes (980 Watts)
Interface Port(s) DB-9 RS-232,SmartSlot,USB
Available SmartSlot™ Interface Quantity
Control panel LED status display with load and battery bar-graphs and On Line : On Battery : Replace Battery : and Overload Indicators Audible Alarm
Alarm when on battery : distinctive low battery alarm : configurable delays
Surge energy rating 480 Joules
Filtering Full time multi-pole noise filtering
2.8 | Laser printer A4 |  | pcs | 1
2 | CCC2 DIREKCIJA - TOTAL | Sub-total carried to Summary I
3 | CCC3 MAJDEVO
3.1 | Establishing of the command and control centre CCC3 Majdevo for the regional water supply system |  | set | 1
o furbishing of the centre
3.2 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Terminal unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width: 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used: IP V4, UDP, TCP, IC MP, Telnet, HTTP, FTP, SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Wind resistance 190 km/hr
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 1
Radio-device power supply, 90-220VAC/24VDC, min 0,3 A, indoor construction, with Ethernet by-pass pcs 1
Ethernet Surge Suppressor , for outdoor installation pcs 1
FTP cable cat.5e, patch, 30m pcs 1
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Radio-device and control module outdoor installation pcs 1
Set-up and configuration of radio-device and control module pcs 1
unspecified consumables pcs 1
Travel and accommodation expenses pcs 1
System commissioning pcs 1
Unspecified material pcs 1
3.3 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
3.4 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
3.5 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
3.6 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the WTP building, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
3.7 | Reconstruction of the existing control panel and command board. |  | set | 1
The existing acquisition devices MAP8 are to be connected to the PLC's communication module, via a RS485 fieldbus,
Signals concerning PS Majdevo, PS Aleksandrovac and PS Nabrđe should be directly connected to I/O modules of the PLC-1.3, providing remote monitoring and control of these sites, which further means:
o install three rotary 3-pole 1-0-2 switches for local-remote operation mode selection,
o reconnect command circuitry in order to provide operation mode selection, remote control from the distribution cabinet ROMTK and signal monitoring to the ROMTK,
o install auxiliary relays for contact multiplication:
K1 Two-pole relay 220VAC, PGR3131, 2P, 230V/12A, PT270730, socket YPT78702,
K2...K5 Single pole relays G2RV-SL700 AC230.
o install DIN Rail Mounting Wire Terminal Blocks-Clamps, 600V/25A rated, for stranded wire up to 2.5mm2 or solid wire up to 4mm2 pcs 27
o install accessories: cable lugs, cable end sleeves, stranded isolated wire 1.5mm2and 2.5mm2, heat shrink, cable tags, device identification marks etc. set 1
o install, label and connect signal cables between control panel/command board and ROMTK.
3.8 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the command room.
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested.
The distribution cabinet ROMTK contains:
U1 PLC CJ1M-CPU13, 1xSCU41, 1xETN21, 1xAD041-v1, 4xID211, 1xOD212
U2 UPS SLAC24
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U7 Radio-modem T-96SR
U8 Over voltage protection FRD24 HF
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection VF230
U12 Aerial surge protection
Q0 Rotary switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...64 Single-pole interface relay 220VAC: G2RV-SLC700 AC230
K91...96 Single-pole interface relay 24VDC: G2RV-SLC700 DC24
X1,2,3,4 DIN Rail Mounting Terminal Blocks-Clamps, 600V/25A, for stranded wire up to 2.5mm2 or solid wire up to 4mm2
Accessories: PVC wiring ducts 60mm wide, cable lugs, cable end sleeves, stranded isolated wire 1.5mm2, heat shrink tubing, cable tags, device identification marks, earth- and neutral busbars etc.
3.9 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
UPS mentioned as a part of ROMTK distribution cabinet, with the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah - pcs 2
All mounted in the CCMS cabinet ROMTK Complete
3.10 | Programmable Logic Controller PLC1.3: type CJ1M |  | set | 1
The existing PLC configuration from CCC2 Direkcija will be moved into the CCC3 Majdevo. The following modules must be added to it:
CJ1W-ETN21 pcs 1
CJ1W-ID211 NL pcs 4
CJ1W-OD212 pcs 1
CJ1W-AD041-V1 NL pcs 1
3.11 | The application software for PLC-1.3 should provide: |  | set | 1
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. regular data polling of acquisition devices MAP8, with polling time not longer than 30s,
c. servicing data requests from the authorised command centre PLC-4.12 on the radio-modem network and sending replies with the most recent data, including those retrieved from acquisition devices MAP8 and those obtained directly through its own I/O modules
d. servicing command messages from the authorised command centre,
e. direct pump control for PS Majdevo (7.5kW), PS Aleksandrovac (90kW) and PS Nabrđe (15kW), in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
f. continuous execution of protective procedures for the equipment in PS Majdevo, PS Aleksandrovac and PS Nabrđe,
d. self-diagnostic tests and placement of results in the main storage area.
All aforementioned functions as anticipated in the Technical Report.
3.12 | Expanding the existing LAN and UTP cabling |  | set | 1
Expanding and configuring of the existing LAN in order to incorporate two monitoring stations and to integrate LAN into the CCMS WAN
3.13 | The monitoring station for the operator in CCC3 Majdevo |  | pcs | 1
A PC computer of the following characteristics:
KC C2D8400,2GB,2x500 GB
LGA775, P35+ICH9, FSB 1333/1066/800, PCI-E X16,
4xDual Channel DDRII, 3PCI, 3PCI-E, SB, PCI-E
GiGaBit Lan, 6xSATAII, 1xPATA, 1xPATA, RAID
1,0,5,10, Virtual Dual BIOS, ATX, RoHSGA-EP43-DS3LR
LGA775 E8200 Intel
DDR2- 800 MHz, 1GB PC 6400
DDR2- 800 MHz, 1GB PC 6400
500GB,7200rpm, SATA II, 16MBWD5000A AKS WD
500GB,7200rpm, SATA II, 16MBWD5000A AKS WD
DVD RW 20x speed, black, bulk, SecureDisc GSAH55N RBB LG
ATI VGA HD 2400 PRO 256M GDDR3 PCI-E DUAL DVI-IHD 2900PRO 512M PALIT
Mini Tower ATX 450 W ,USB,Audio,Black TLA 481 Foxconn
Mouse, PS2 Optical S90
Keyboard PS2,black Deluxe 250
Windows XP Professional OEM CD
3.14 | The operator monitoring station's computer monitor |  | pcs | 1
Panel Viewable area 22" Wide; Brightness 300 cd/m²
Contrast Ratio 1000:1 ; Viewing Angle (H/V) 170˚/160˚ (CR>10)
Response Time (ms) 5 - ; Maximum Resolution 1680 x 1050
Colour Supported 16.7 Mil.
Signal Input Input Video Signal Analog RGB
Sync Type Separate H/V, Composite, SOG
Input Connectors 15pin D-SUB
Plug & Play DDC 2B
USB powered hub option
Mac compatibility Yes
Power On Mode 46 Watts (Max.)
DPMS Mode <1 Watt
Type Built-in
Multimedia Speakers 2 W x 2
Wall-Mount VESA 10
3.15 | The monitoring station for the WTP general manager |  | pcs | 1
A PC computer of the following characteristics:
KC C2D8400,2GB,2x500 GB
LGA775, P35+ICH9, FSB 1333/1066/800, PCI-E X16,
4xDual Channel DDRII, 3PCI, 3PCI-E, SB, PCI-E
GiGaBit Lan, 6xSATAII, 1xPATA, 1xPATA, RAID
1,0,5,10, Virtual Dual BIOS, ATX, RoHSGA-EP43-DS3LR
LGA775 E8200 Intel
DDR2- 800 MHz, 1GB PC 6400
500GB,7200rpm, SATA II, 16MBWD5000A AKS WD
DVD RW 20x speed, black, bulk, SecureDisc GSAH55N RBB LG
ATI VGA HD 2400 PRO 256M GDDR3 PCI-E DUAL DVI-IHD 2900PRO 512M PALIT
Mini Tower ATX 450 W, USB, Audio, Black TLA 481
Mouse, PS2 Optical S90
Keyboard PS2,black Deluxe 250
Windows XP Professional OEM CD
3.16 | The computer monitor for WTP general manager's computer |  | pcs | 1
One 19" TFT monitor:
Panel Viewable area 19" Wide; Brightness 300 cd/m² Contrast Ratio 1000:1 ; Viewing Angle (H/V) 170˚/160˚ (CR>10) Response Time (ms) 5 - ; Maximum Resolution 1680 x 1050 Colour Supported 16.7 Mil. Signal Input Input Video Signal Analog RGB Sync Type Separate H/V, Composite, SOG Input Connectors 15pin D-SUB Plug & Play DDC 2B USB powered hub option Mac compatibility Yes Power On Mode 46 Watts (Max.) DPMS Mode <1 Watt Type Built-in Multimedia Speakers 2 W x 2 Wall-Mount VESA 10
3.17 | Delivery, installation and commissioning of the UPS for the monitoring station |  | pcs | 2
Output Power Capacity 980 Watts / 1500 VA
Max Configurable Power 980 Watts / 1500 VA
Nominal Output Voltage 230V
Output Voltage Note Configurable for 220 : 240 V
Output Voltage Distortion Less than 5% at full load
Output Frequency (sync to mains) 47 - 53 Hz for 50 Hz nominal,
Crest Factor up to 5 : 1
Waveform Type Sine wave
Output Connections IEC 320 C13
Nominal Input Voltage 230V
Input Frequency 50/60 Hz +/- 3 Hz (auto sensing)
Input voltage range for main operations 160 - 286V
Input voltage adjustable range for mains operation 151 - 302V
Battery Type Maintenance-free sealed Lead-Acid battery
Typical recharge time 3 hours
Typical Backup Time at Half Load 23.9 minutes (490 Watts)
Typical Backup Time at Full Load 6.7 minutes (980 Watts)
Interface Port(s) DB-9 RS-232,SmartSlot,USB
Available SmartSlot™ Interface Quantity
Control panel LED status display with load and battery bar-graphs and On Line : On Battery : Replace Battery : and Overload Indicators Audible Alarm
Alarm when on battery : distinctive low battery alarm : configurable delays
Surge energy rating 480 Joules
Filtering Full time multi-pole noise filtering
3.18 | Software upgrade for the existing acquisition devices, connecting the existing acquisition devices into the CCMS. |  | set | 1
3 | CCC3 MAJDEVO – TOTAL | Sub-total carried to Summary I
5 | CCC5 CELIJE (CELIJE DAM)
5.1 | Establishing of the command and control centre CCC5 Ćelije for the regional water supply system |  | set | 1
o furbishing of the centre.
The centre will be establish on the premises of the existing command centre for the Ćelije dam, in the control room within the main management building.
5.2 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Terminal unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width: 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used: IP V4, UDP, TCP, IC MP, Telnet, HTTP, FTP, SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Wind resistance 190 km/hr
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 1
Radio-device power supply, 90-220VAC/24VDC, min 0,3 A, indoor construction, with Ethernet by-pass pcs 1
Ethernet Surge Suppressor , for outdoor installation pcs 1
FTP cable cat.5e, patch, 30m pcs 1
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Radio-device and control module outdoor installation pcs 1
Set-up and configuration of radio-device and control module pcs 1
unspecified consumables pcs 1
Travel and accommodation expenses pcs 1
System commissioning pcs 1
Unspecified material pcs 1
5 | KKC5 CELIJE - TOTAL | Sub-total carried to Summary I
6 | SOFTWARE SUPPORT
The software packages for the CCMS must be comaptible with the software packages already installed within the existing CCMS. These existing packages will remain the part of the new CCMS, upgraded where necessary.
6.1 | CCC1 Lipovac - the main server run-time SCADA software package. This real-time server-client run-time must provide: |  | pcs | 1
o necessary support for the Modbus ASCII and Modbus/TCP data protocols;
o regular data retrieve from PLCs over a serial connection and Ethernet TCP/IP, using the defined protocols;
o regular update of aggregate and derived data;
o client authorisation;
o at least three levels of access rights: monitor only, monitor and control, supervisor;
o services to client data requests and command messages over Ethernet TCP/IP;
o ability to post regular data requests to another server in the system;
o ability to serve client commands, either by executing them or routing them to the Master PLC;
o ability to accept and archive manually entered data form monitoring stations, usually results of laboratory analysis;
o ability to accept and execute real-time requests for acquisition parameter changes and to record all of the changes in the internal database;
o unconstrained number of tags, both analogue and digital, input and output;
o alarming mechanism, limit and signal alarm detection, alarm trip, normalisation and acknowledgement detection;
o notification of the clients about new alarm detection;
o event, system event and operator actions detection;
o the internal data manager and the internal database;
o the real-time archiving of all variables, measurements, statuses, alarms, events and actions;
o aggregate and statistical report data generation, upon reception of the client request;
o historical data export, upon client request;
o all of aforementioned possibilities must be fully configurable, especially timings, tags, alarms, events, actions, data retreive/exchange parameters and reports;
The software must be Windows XP based.
6.2 | CCC1 Lipovac - the monitoring station's run-time SCADA software package. Client SCADA run-time must provide: |  | pcs | 6
o client/server communication services towards the server, using Ethernet TCP/IP and compatible data format;
o user interface support;
o authorisation support;
o posting of regular data requests to the server over Ethernet TCP/IP;
o real-time data presentation on form of a high resolution mimic diagrams;
o historical data presentation in the form of trends and lists;
o posting of a command messages to the server upon user interaction;
o posting of a alarm request upon the reception of alarm notification message from the server;
o posting an aggregate or statistical data request to the server upon user command;
o presentation of aggregate or statistical reports upon data arrival from the server;
o posting of a data export request, upon user command;
o basic data management support for caching valid historical data, obtained from the server;
o data management support for an independent local database, for object-oriented non real-time data;
o all of aforementioned possibilities must be fully configurable, especially data exchange parameters, mimic diagrams and reports;
The software must be Windows XP based.
6.3 | CCC2 Direkcija - the monitoring station's run-time SCADA software package. |  | pcs | 1
6.4 | CCC3 Majdevo - the monitoring station's run-time SCADA software package. |  | pcs | 2
6.5 | The application software for the main server in CCC1 Lipovac |  | set | 1
The application software packages for subsystems or distribution networks are itemized in a section of the bill concerning these objects, thus making it suitable for partial construction.
The application software for the main server should comply with the demands in the Technical Report
6.6 | The application software for the monitoring stations in CCC1 Lipovac |  | set | 6
The application software for the monitoring stations in CCC1 Lipovac should provide visualisation of entire regional water supply system, by means of 88 mimic diagrams and number of aggregate reports. Also, this software will provide means of operational control of entire system. Detailed survey can be found in the Technical Report.
6.7 | Upgrade of two existing monitoring stations' application software, the application software for one new monitoring station in CCC2 Direkcija |  | set | 1
Two existing monitoring stations in CCC12 Direkcija are to be reconfigured, while the new monitoring station in the Technical Manager office should be equipped with the new instance of the SCADA application. Eventually, all three stations should provide visualisation of entire regional water supply system, by means of 88 mimic diagrams and number of aggregate reports. Also, this software will provide operational control possibility of entire system. Detailed survey can be found in the Technical Report.
6.8 | The application software for the monitoring station in CCC3 Majdevo |  | set | 2
The application software for the monitoring station in CCC3 Majdevo should provide visualisation of entire subsystem "The Regional System", three distribution networks DN Majdevo, DN Aleksandrovac and DN Nabrđe and basic measurements within WTP Majdevo, by means of 15 mimic diagrams and appropriate number of aggregate reports. Also, the software should provide means of operational control of aforementioned distribution networks. Detailed survey can be found in the Technical Report.
6.9 | Upgrade of the existing monitoring station application software in CCC4 Bagdala |  | set | 1
Reconfigure the existing SCADA package in CCC4 Bagdala in order to provide data exchange between the monitoring station and the main server in CCC1 Lipovac, instead of PLC-1.7, as it is now the case. This monitoring station should retain its present monitoring and control capabilities. Detailed survey can be found in the Technical Report.
6.10 | Upgrade of the existing monitoring station application software in CCC5 Ćelije |  | set | 1
Reconfigure the existing SCADA package in CCC5 Ćelije in order to provide full client-server communication and bi-directional data exchange with the main server in CCC1 Lipovac. Data should be exchanged regularly each 30s. Data exchange should include all the data from the Ćelije dam and an predefined data set from the regional water supply system. An additional mimic diagram should be configured for the regional system data presentation, with no control capabilities. Detailed survey can be found in the Technical Report.
6 | SOFTWARE SUPPORT - TOTAL | Sub-total carried to Summary I
7 | AS-BUILT DOCUMENTATION
7.1 | The production and assembly of as-built documentation KS DP09 |  | set | 1
for the command and control centres.
7 | AS-BUILT DOCUMENTATION - TOTAL | Sub-total carried to Summary I
8 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
8.1 | Parameter adjustment and putting into operation communication links between command and control centres. |  | set | 1
Parameter adjustment, testing and putting into operation measuring equipment, automation systems and remote controls.
Commissioning and performance verification
Putting into trial operation
The trial operation will last 15 days
8 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION - TOTAL | Sub-total carried to Summary I
| SUMMARY I. - COMMAND AND CONTROL CENTRES |  |  |  |  | Amount (euro)
1 | CCC1 LIPOVAC
2 | CCC2 DIREKCIJA
3 | CCC3 MAJDEVO
5 | CCC5 CELIJE
6 | SOFTWARE SUPPORT
7 | AS-BUILT DOCUMENTATION PRODUCTION
8 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
I | COMMAND AND CONTROL CENTRES | TOTAL carried to Summary A.
II | METERING AND REGULATION STATIONS
10 | MRS LIPOVAC
10.1 | Reconstruction of the command object containing control, measurement and communication equipment, which means: |  | set | 1
o construction of a ceiling and a proper roof,
o external wall insulation and rendering,
o construction of side walkways,
o lightning protection and earthing installation,
o interior and exterior lighting installation.
10.2 | Reconstruction of the valve control cabinet RO |  | set | 1
Inspect in detail valve control cabinet RO in order to bring it in accordance with the existing design documentation.
Reconnect the existing command circuitry to provide: - remote valve control from the CCMS cabinet, - effective control by intermediary PLC-1.5 even in local operation mode, slowing down valve actuator movements,
- necessary monitoring signals for the existing CCMS cabinet. Connect the valve control cabinet and the existing CCMS cabinet.
10.3 | Supply, delivery and wiring of an additional module for the PLC-1.5, type CJ1M |  | pcs | 1
Power supply unit: CJ1W-PD025
10.4 | Upgrade of the PLC -1.5 application software |  | set | 1
Re-programme the existing PLC:
o eliminate the existing downstream pressure control algorithm in remote operation mode,
o incorporate logic for the support of a downstream reservoir level control algorithm,
o adapt bumpless transfer logic to support all control algorithms and all operation modes,
o provide that auxiliary logic for slowing down valve actuator motions is active in all control algorithms and all operation modes, including local operation mode, when PLC is an intermediary between the operator and the actuators,
o provide necessary communication functions,
10.5 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The existing UPS in the CCMS cabinet must be replaced with an UPS with the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah - pcs 2
All mounted in the CCMS cabinet ROMTK Complete
10.6 | Putting into operation the existing radio-communication equipment |  | set | 1
o connect previously delivered radio-modem DATARADIO T96SR to the PLC-1.5.
o adjust radio-modem frequency,
o provide communication link to the authorised communication centre PLC-3.8.
10 | MRS LIPOVAC - TOTAL | Sub-total carried to Summary II
11 | MRS KRUSEVAC (MAKRESANE)
11.1 | Supply, delivery and wiring of the PLC-1.9, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 3
CJ1W-OD212 pcs 1
CJ1W-AD081-V1 NL pcs 1
11.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB B908 Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
11.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
11.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
11.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
11.6 | The PLC-1.9 application software |  | set | 1
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct regulation valve control in remote operation modes. In remote automatic operation mode, three remotely selectable control algorithms are available: inlet pressure control algorithm, outlet pressure control algorithm and flow control algorithm. Protective functions are active in all remote operation modes,
c. communication services to client data requests or command messages, coming from the authorised communication centre PLC-1.7,
d. diagnostic functions for measuring equipment and the PLC itself.
11.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
11.8 | Supply, delivery, installation and commissioning of the main distribution cabinet GRO, wall mounted inside MRS |  | set | 1
The distribution cabinet GRO should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the GRO in MRS.
The installed equipment inside the cabinet will provide:
o AC mains distribution for the MRS,
o local or remote operation mode selection, by means of a rotary multi-pole multi-position switch 1-0-2 meaning "Local-0-Remote",
o pushbutton valve control in local operation mode,
o valve control in remote operation mode by means of external voltage-free contacts,
o all necessary actuator and valve protections (limit and torque switches, thermal protections, motor protection circuit breaker)
o local indication of valve status and position,
o all necessary monitoring signals for the separate CCMS distribution cabinet (ROMTK), by means of auxiliary contacts, relays and wire terminals.
The cabinet contains:
Q0 Three-pole switch PGR4360 LTS 25 EH4 A3
F00 Main circuit breaker PGR4480 SI C25/3
F01,F02 Motor circuit breaker protection BE5-1.6, BE5-NHI-E-11
K11,K12 Motor contactors K3-10A10 230,HN10, HN01
K21,K22 Motor contactors K3-10A10 230,HN10, HN01
U1 AC line monitor 71.31.8.400.2000
U2,U3 Analogue indicator 4-20mA, 0-100%
F03 Circuit breaker PGR4470 SI C10/3
F04,05,06,07,08 Circuit breaker PGR4470 SI C10/1
F09,F10 Circuit breaker PGR4470 SI C6/1
Q1 Three-pole switch 20A/1-0/3P/V M10HEA3
T11,T12 Pushbuttons 230VAC, 2A, BS4D SW
T21,T22 Pushbuttons 230VAC, 2A, BS4D SW
K13,14,15 Single pole relays 220VAC, G2RV-SLC700 AC230
K23,24,25 Single pole relays 220VAC, G2RV-SLC700 AC230
MP Open door detector
H0 Interior cabinet lighting 220VAC
T Thermostat
G Anti-condensation heater
H11,12,13,14,15,16 Signal indicator 220VAC, B3-MB230 RT/GN
H21,22,23,24,25,26 Signal indicator 220VAC, B3-MB230 RT/GN
X0 Wire terminal, 5 clamps, 4mm2
X1 Wire terminal, 16 clamps, 2.5mm2
X2 Wire terminal, 31 clamps, 2.5mm2
X3 Wire terminal, 30 clamps, 2.5mm2
X4 Wire terminal, 4 clamps, 2.5mm2
Complete
11.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object.
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in MRS.
The cabinet contains:
U1 PLC CJ1M-CPU11, 3xDI211, 1xOC201, 1XAD081-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Over voltage protection LPP4
U6 Digital display DP3v5
U7 Digital display DP3v5
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
U15 Electromagnetic flow meter
U16 Electromagnetic flow meter
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K21 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K50..K62 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1,2,3,4 Wire terminals 2.5mm2
Complete
11.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
11.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
11.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for inlet and outlet pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors and limit pressure switches.
11.13 | Supply, delivery and installation of limit pressure detector |  | pcs | 2
Electric contact manometer with two adjustable limit switches, used for alarming, type Teleoptik or equivalent
Measuring range : 0-16 bar
Fitting: 0.5 inch
11.14 | Supply, delivery and installation of absolute pressure transmitters |  | pcs | 2
Compact version
CHARACTERISTICS
• Available ranges (0... 10 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
11.15 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
11.16 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o installation of feeding pipe 6/4" and ball valve 6/4"
11.17 | Installation, wiring and putting into operation of two |  | set | 2
electromagnetic flow meter DN350 NP16, one on each hydraulic line of the MRS
Type Logomer 28
Sensor: log probe f 28mmm
Fitting: feeding pipe 6/4" ball valve 6/4"
Accuracy: 1%
Transducer (IC620F) for wall mounting, with a LCD showing both flow rate and flow total, communication ports RS232 and RS485, current output 4-20mA, 13 bits AD resolution, pulse output, alarming capabilities.
Power supply 220VAC 50Hz
Sensor protection degree IP68
Equipment is already purchased within the previous investment, but not installed.
11.18 | Supply, delivery, installation and wiring of a conductive level detector valve chamber flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
11.19 | Cable delivery, installation and connecting |  | set | 1
Delivery and installation of power cables inside MRS for interior lighting and socket supply. Cables are to be installed out-of-walls using clamps.
Cable installation also includes cable end preparation and labelling, cable connecting and/or splicing and junction boxes installation.
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00Y 3x2.5 10 Power supply 220VAC, 50Hz
W01 PP00Y 3x2.5 20 Flow meter supply 220VAC
W02 PP00Y 3x2.5 20 Flow meter supply 220VAC
W03 IyStY 15x2x0.6 10 ROMTK to GRO
W04 IyStY 1x2x0.6 20 To flooding detector probes
W05 IyStY 1x2x0.6 40 Open door detector
W06 IyStY 2x2x0.6 30 Isolation valve SV1 limit switch
W07 IyStY 2x2x0.6 30 Isolation valve SV2 limit switch
W08 IyStY 2x2x0.6 30 Isolation valve SV3 limit switch
W09 IyStY 2x2x0.6 30 Isolation valve SV4 limit switch
W10 IyStY 2x2x0.6 25 Inlet limit pressure detector
W11 IyStY 2x2x0.6 25 Outlet limit pressure detector
W12 LiYCy 2x0.75 25 To inlet pressure sensor
W13 LiYCy 2x0.75 25 To outlet pressure sensor
W14 LiYCy 2x0.75 25 To line 1 flow meter
W15 LiYCy 2x0.75 25 To line 2 flow meter
W16 LiYCy 4x0.75 25 To V1 position transducer
W17 LiYCy 4x0.75 25 To V2 position transducer
W100 LiYCy 8x0.6 2 Comm. cable, PLC-T96SR
W101 Antenna cable
11.20 | Electrical installation services |  | set | 1
The separate distribution cabinet with power inlet and power meter unit is assumed to be installed by authorised EPS personal (EPS stands for Public Enterprise ”Electric power industry of Serbia”).
Setting and tightening of electric installation accessories in the MRS, i.e. junction boxes, switches and lights. Connecting and functional testing.
Accessories:
Single-phase switch 220VAC 10A, in silumin case pcs 3 Single phase out-of-wall power socket (receptacle) 16A pcs 2 Three phase out-of-wall power socket 16A pcs 1
Flat type deck lighting fixture with incandescent bulb 200W, IP55, type BRODSKA 2 or equivalent pcs 3
Other unspecified accessories and works
Complete.
11 | MRS KRUSEVAC (MAKRESANE) - TOTAL | Sub-total carried to Summary II
12 | MRS STALAC
12.1 | Supply, delivery and wiring of the PLC-1.11, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 3
CJ1W-OD212 pcs 1
CJ1W-AD081-V1 NL pcs 1
12.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
12.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
12.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
12.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
12.6 | The PLC-1.11 application software |  | set | 1
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct regulation valve control in remote operation modes. In remote automatic operation mode, three remotely selectable control algorithms are available: outlet pressure control algorithm, flow control algorithm and downstream reservoir level control algorithm. Protective functions are active in all remote operation modes,
c. communication services to client data requests or command messages, coming from the authorised communication centre PLC-1.7,
d. diagnostic functions for measuring equipment and the PLC itself.
12.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
12.8 | Supply, delivery, installation and commissioning of the main distribution cabinet GRO, wall mounted inside MRS |  | set | 1
The distribution cabinet GRO should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the GRO in MRS.
The installed equipment inside the cabinet will provide:
o AC mains distribution for the MRS,
o local or remote operation mode selection, by means of a rotary multi-pole multi-position switch 1-0-2 meaning "Local-0-Remote",
o pushbutton valve control in local operation mode,
o valve control in remote operation mode by means of external voltage-free contacts,
o all necessary actuator and valve protections (limit and torque switches, thermal protections, motor protection circuit breaker)
o local indication of valve status and position,
o all necessary monitoring signals for the separate CCMS distribution cabinet (ROMTK), by means of auxiliary contacts, relays and wire terminals.
The cabinet contains:
Q0 Three-pole switch PGR4360 LTS 25 EH4 A3
F00 Main circuit breaker PGR4480 SI C25/3
F01,F02 Motor circuit breaker protection BE5-1.6, BE5-NHI-E-11
K11,K12 Motor contactors K3-10A10 230,HN10, HN01
K21,K22 Motor contactors K3-10A10 230,HN10, HN01
U1 AC line monitor 71.31.8.400.2000
U2,U3 Analogue indicator 4-20mA, 0-100%
F03 Circuit breaker PGR4470 SI C10/3
F04,05,06,07,08 Circuit breaker PGR4470 SI C10/1
F09,F10 Circuit breaker PGR4470 SI C6/1
Q1 Three-pole switch 20A/1-0/3P/V M10HEA3
T11,T12 Pushbuttons 230VAC, 2A, BS4D SW
T21,T22 Pushbuttons 230VAC, 2A, BS4D SW
K13,14,15 Single pole relays 220VAC, G2RV-SLC700 AC230
K23,24,25 Single pole relays 220VAC, G2RV-SLC700 AC230
MP Open door detector
H0 Interior cabinet lighting 220VAC
T Thermostat
G Anti-condensation heater
H11,12,13,14,15,16 Signal indicator 220VAC, B3-MB230 RT/GN
H21,22,23,24,25,26 Signal indicator 220VAC, B3-MB230 RT/GN
X0 Wire terminal, 5 clamps, 4mm2
X1 Wire terminal, 16 clamps, 2.5mm2
X2 Wire terminal, 31 clamps, 2.5mm2
X3 Wire terminal, 30 clamps, 2.5mm2
X4 Wire terminal, 4 clamps, 2.5mm2
Complete
12.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object.
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in MRS.
The cabinet contains:
U1 PLC CJ1M-CPU11, 3xDI211, 1xOC201, 1XAD081-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Over voltage protection LPP4
U6 Digital display DP3v5
U7 Digital display DP3v5
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
U15 Electromagnetic flow meter
U16 Electromagnetic flow meter
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K21 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K50..K62 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1,2,3,4 Wire terminals 2.5mm2
Complete
12.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah - pcs 2
All mounted in the ROMTK cabinet Complete
12.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
12.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for inlet and outlet pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors and limit pressure switches.
12.13 | Supply, delivery and installation of limit pressure detector |  | pcs | 2
Electric contact manometer with two adjustable limit switches, used for alarming, type Teleoptik or equivalent
Measuring range : 0-16 bar
Fitting: 0.5 inch
12.14 | Supply, delivery and installation of absolute pressure transmitters |  | pcs | 2
Compact version
CHARACTERISTICS
• Available ranges (0... 10 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
12.15 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
12.16 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND150 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
12.17 | Delivery, installation and commissioning of an electromagnetic flowmeter Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics Nominal diameters DN 150 Hard rubber or polyurethane lining High accuracy: ± 0.5% (option: ± 0.2%) Robust field housing, IP 67 wall-mount housing for straightforward Class 0.30 Linearity 0.1 Repeatability 0.1 Power supply: 24VDC ; power consumption: <5W Display: 122x32 dots LCD graphical display with backlight Configuring: numerical via keypad, range, measurement unit,sensitivity etc. Output: galvanically insulated from the other circuits ; Insulation: R > 100 Mohm, V > 1500 V Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Switch outputs: pulse for external totalizer, 0.1A, 250V photorelay configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay Sensor input: type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit oversampling: x100 ; sensitivity:0.1 uV Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit Ambient temperature: -20…+70 0C Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK |  | set | 2
12.18 | Supply, delivery, installation and wiring of a conductive level detector valve chamber flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
12.19 | Cable delivery, installation and connecting |  | set | 1
Delivery and installation of power cables inside MRS for interior lighting and socket supply. Cables are to be installed out-of-walls using clamps.
Cable installation also includes cable end preparation and labelling, cable connecting and/or splicing and junction boxes installation.
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00Y 3x2.5 10 Power supply 220VAC, 50Hz
W01 PP00Y 3x2.5 20 Flow meter supply 220VAC
W02 PP00Y 3x2.5 20 Flow meter supply 220VAC
W03 IyStY 15x2x0.6 10 ROMTK to GRO
W04 IyStY 1x2x0.6 20 To flooding detector probes
W05 IyStY 1x2x0.6 40 Open door detector
W06 IyStY 2x2x0.6 30 Isolation valve SV1 limit switch
W07 IyStY 2x2x0.6 30 Isolation valve SV2 limit switch
W08 IyStY 2x2x0.6 30 Isolation valve SV3 limit switch
W09 IyStY 2x2x0.6 30 Isolation valve SV4 limit switch
W10 IyStY 2x2x0.6 25 Inlet limit pressure detector
W11 IyStY 2x2x0.6 25 Outlet limit pressure detector
W12 LiYCy 2x0.75 25 To inlet pressure sensor
W13 LiYCy 2x0.75 25 To outlet pressure sensor
W14 LiYCy 2x0.75 25 To line 1 flow meter
W15 LiYCy 2x0.75 25 To line 2 flow meter
W16 LiYCy 4x0.75 25 To V1 position transducer
W17 LiYCy 4x0.75 25 To V2 position transducer
W100 LiYCy 8x0.6 2 Comm. cable, PLC-T96SR
W101 Antenna cable
12.20 | Electrical installation services |  | set | 1
The separate distribution cabinet with power inlet and power meter unit is assumed to be installed by authorised EPS personal (EPS stands for Public Enterprise ”Electric power industry of Serbia”).
Setting and tightening of electric installation accessories in the MRS, i.e. junction boxes, switches and lights. Connecting and functional testing.
Accessories:
Single-phase switch 220VAC 10A, in silumin case pcs 3 Single phase out-of-wall power socket (receptacle) 16A pcs 2 Three phase out-of-wall power socket 16A pcs 1
Flat type deck lighting fixture with incandescent bulb 200W, IP55, type BRODSKA or equivalent pcs 3
Other unspecified accessories and works
Complete.
12 | MRS STALAC - TOTAL | Sub-total carried to Summary II
13 | MRS VARVARIN
13.1 | Supply, delivery and wiring of the PLC-1.12, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 3
CJ1W-OD212 pcs 1
CJ1W-AD081-V1 NL pcs 1
13.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
13.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
13.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
13.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
13.6 | The PLC-1.12 application software |  | set | 1
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct regulation valve control in remote operation modes. In remote automatic operation mode, three remotely selectable control algorithms are available: outlet pressure control algorithm, flow control algorithm and downstream reservoir level control algorithm. Protective functions are active in all remote operation modes,
c. communication services to client data requests or command messages, coming from the authorised communication centre PLC-1.7,
d. diagnostic functions for measuring equipment and the PLC itself.
13.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
13.8 | Supply, delivery, installation and commissioning of the main distribution cabinet GRO, wall mounted inside MRS |  | set | 1
The distribution cabinet GRO should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the GRO in MRS.
The installed equipment inside the cabinet will provide:
o AC mains distribution for the MRS,
o local or remote operation mode selection, by means of a rotary multi-pole multi-position switch 1-0-2 meaning "Local-0-Remote",
o pushbutton valve control in local operation mode,
o valve control in remote operation mode by means of external voltage-free contacts,
o all necessary actuator and valve protections (limit and torque switches, thermal protections, motor protection circuit breaker)
o local indication of valve status and position,
o all necessary monitoring signals for the separate CCMS distribution cabinet (ROMTK), by means of auxiliary contacts, relays and wire terminals.
The cabinet contains:
Q0 Three-pole switch PGR4360 LTS 25 EH4 A3
F00 Main circuit breaker PGR4480 SI C25/3
F01,F02 Motor circuit breaker protection BE5-1.6, BE5-NHI-E-11
K11,K12 Motor contactors K3-10A10 230,HN10, HN01
K21,K22 Motor contactors K3-10A10 230,HN10, HN01
U1 AC line monitor 71.31.8.400.2000
U2,U3 Analogue indicator 4-20mA, 0-100%
F03 Circuit breaker PGR4470 SI C10/3
F04,05,06,07,08 Circuit breaker PGR4470 SI C10/1
F09,F10 Circuit breaker PGR4470 SI C6/1
Q1 Three-pole switch 20A/1-0/3P/V M10HEA3
T11,T12 Pushbuttons 230VAC, 2A, BS4D SW
T21,T22 Pushbuttons 230VAC, 2A, BS4D SW
K13,14,15 Single pole relays 220VAC, G2RV-SLC700 AC230
K23,24,25 Single pole relays 220VAC, G2RV-SLC700 AC230
MP Open door detector
H0 Interior cabinet lighting 220VAC
T Thermostat
G Anti-condensation heater
H11,12,13,14,15,16 Signal indicator 220VAC, B3-MB230 RT/GN
H21,22,23,24,25,26 Signal indicator 220VAC, B3-MB230 RT/GN
X0 Wire terminal, 5 clamps, 4mm2
X1 Wire terminal, 16 clamps, 2.5mm2
X2 Wire terminal, 31 clamps, 2.5mm2
X3 Wire terminal, 30 clamps, 2.5mm2
X4 Wire terminal, 4 clamps, 2.5mm2
Complete
13.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object.
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in MRS.
The cabinet contains:
U1 PLC CJ1M-CPU11, 3xDI211, 1xOC201, 1XAD081-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Over voltage protection LPP4
U6 Digital display DP3v5
U7 Digital display DP3v5
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
U15 Electromagnetic flow meter
U16 Electromagnetic flow meter
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K21 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K50..K62 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1,2,3,4 Wire terminals 2.5mm2
Complete
13.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
13.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
13.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for inlet and outlet pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors and limit pressure switches.
13.13 | Supply, delivery and installation of limit pressure detector |  | pcs | 2
Electric contact manometer with two adjustable limit switches, used for alarming, type Teleoptik or equivalent
Measuring range : 0-16 bar
Fitting: 0.5 inch
13.14 | Supply, delivery and installation of absolute pressure transmitters |  | pcs | 2
Compact version
CHARACTERISTICS
• Available ranges (0... 10 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
13.15 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
13.16 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND250 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
13.17 | Delivery, installation and commissioning of an electromagnetic flowmeter Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics Nominal diameters DN 250 Hard rubber or polyurethane lining High accuracy: ± 0.5% (option: ± 0.2%) Robust field housing, IP 67 wall-mount housing for straightforward Class 0.30 Linearity 0.1 Repeatability 0.1 Power supply: 24VDC ; power consumption: <5W Display: 122x32 dots LCD graphical display with backlight Configuring: numerical via keypad, range, measurement unit,sensitivity etc. Output: galvanically insulated from the other circuits ; Insulation: R > 100 Mohm, V > 1500 V Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Switch outputs: pulse for external totalizer, 0.1A, 250V photorelay configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay Sensor input: type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit oversampling: x100 ; sensitivity:0.1 uV Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit Ambient temperature: -20…+70 0C Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK |  | set | 2
13.18 | Supply, delivery, installation and wiring of a conductive level detector valve chamber flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
13.19 | Cable delivery, installation and connecting |  | set | 1
Delivery and installation of power cables inside MRS for interior lighting and socket supply. Cables are to be installed out-of-walls using clamps.
Cable installation also includes cable end preparation and labelling, cable connecting and/or splicing and junction boxes installation.
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00Y 3x2.5 10 Power supply 220VAC, 50Hz
W01 PP00Y 3x2.5 20 Flow meter supply 220VAC
W02 PP00Y 3x2.5 20 Flow meter supply 220VAC
W03 IyStY 15x2x0.6 10 ROMTK to GRO
W04 IyStY 1x2x0.6 20 To flooding detector probes
W05 IyStY 1x2x0.6 40 Open door detector
W06 IyStY 2x2x0.6 30 Isolation valve SV1 limit switch
W07 IyStY 2x2x0.6 30 Isolation valve SV2 limit switch
W08 IyStY 2x2x0.6 30 Isolation valve SV3 limit switch
W09 IyStY 2x2x0.6 30 Isolation valve SV4 limit switch
W10 IyStY 2x2x0.6 25 Inlet limit pressure detector
W11 IyStY 2x2x0.6 25 Outlet limit pressure detector
W12 LiYCy 2x0.75 25 To inlet pressure sensor
W13 LiYCy 2x0.75 25 To outlet pressure sensor
W14 LiYCy 2x0.75 25 To line 1 flow meter
W15 LiYCy 2x0.75 25 To line 2 flow meter
W16 LiYCy 4x0.75 25 To V1 position transducer
W17 LiYCy 4x0.75 25 To V2 position transducer
W100 LiYCy 8x0.6 2 Comm. cable, PLC-T96SR
W101 Antenna cable
13.20 | Electrical installation services |  | set | 1
The separate distribution cabinet with power inlet and power meter unit is assumed to be installed by authorised EPS personal (EPS stands for Public Enterprise ”Electric power industry of Serbia”).
Setting and tightening of electric installation accessories in the MRS, i.e. junction boxes, switches and lights. Connecting and functional testing.
Accessories:
Single-phase switch 220VAC 10A, in silumin case pcs 3 Single phase out-of-wall power socket (receptacle) 16A pcs 2 Three phase out-of-wall power socket 16A pcs 1
Flat type deck lighting fixture with incandescent bulb 200W, IP55, type BRODSKA or equivalent pcs 3
Other unspecified accessories and works
Complete.
13 | MRS VARVARIN - TOTAL | Sub-total carried to Summary II
14 | MRS CICEVAC
14.1 | Supply, delivery and wiring of the PLC-1.13, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 3
CJ1W-OD212 pcs 1
CJ1W-AD081-V1 NL pcs 1
14.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
14.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
14.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
14.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
14.6 | The PLC-1.13 application software |  | set | 1
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct regulation valve control in remote operation modes. In remote automatic operation mode, three remotely selectable control algorithms are available: outlet pressure control algorithm, flow control algorithm and downstream reservoir level control algorithm. Protective functions are active in all remote operation modes,
c. communication services to client data requests or command messages, coming from the authorised communication centre PLC-1.7,
d. diagnostic functions for measuring equipment and the PLC itself.
14.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
14.8 | Supply, delivery, installation and commissioning of the main distribution cabinet GRO, wall mounted inside MRS |  | set | 1
The distribution cabinet GRO should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the GRO in MRS.
The installed equipment inside the cabinet will provide:
o AC mains distribution for the MRS,
o local or remote operation mode selection, by means of a rotary multi-pole multi-position switch 1-0-2 meaning "Local-0-Remote",
o pushbutton valve control in local operation mode,
o valve control in remote operation mode by means of external voltage-free contacts,
o all necessary actuator and valve protections (limit and torque switches, thermal protections, motor protection circuit breaker)
o local indication of valve status and position,
o all necessary monitoring signals for the separate CCMS distribution cabinet (ROMTK), by means of auxiliary contacts, relays and wire terminals.
The cabinet contains:
Q0 Three-pole switch PGR4360 LTS 25 EH4 A3
F00 Main circuit breaker PGR4480 SI C25/3
F01,F02 Motor circuit breaker protection BE5-1.6, BE5-NHI-E-11
K11,K12 Motor contactors K3-10A10 230,HN10, HN01
K21,K22 Motor contactors K3-10A10 230,HN10, HN01
U1 AC line monitor 71.31.8.400.2000
U2,U3 Analogue indicator 4-20mA, 0-100%
F03 Circuit breaker PGR4470 SI C10/3
F04,05,06,07,08 Circuit breaker PGR4470 SI C10/1
F09,F10 Circuit breaker PGR4470 SI C6/1
Q1 Three-pole switch 20A/1-0/3P/V M10HEA3
T11,T12 Pushbuttons 230VAC, 2A, BS4D SW
T21,T22 Pushbuttons 230VAC, 2A, BS4D SW
K13,14,15 Single pole relays 220VAC, G2RV-SLC700 AC230
K23,24,25 Single pole relays 220VAC, G2RV-SLC700 AC230
MP Open door detector
H0 Interior cabinet lighting 220VAC
T Thermostat
G Anti-condensation heater
H11,12,13,14,15,16 Signal indicator 220VAC, B3-MB230 RT/GN
H21,22,23,24,25,26 Signal indicator 220VAC, B3-MB230 RT/GN
X0 Wire terminal, 5 clamps, 4mm2
X1 Wire terminal, 16 clamps, 2.5mm2
X2 Wire terminal, 31 clamps, 2.5mm2
X3 Wire terminal, 30 clamps, 2.5mm2
X4 Wire terminal, 4 clamps, 2.5mm2
Complete
14.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object.
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in MRS.
The cabinet contains:
U1 PLC CJ1M-CPU11, 3xDI211, 1xOC201, 1XAD081-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Over voltage protection LPP4
U6 Digital display DP3v5
U7 Digital display DP3v5
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
U15 Electromagnetic flow meter
U16 Electromagnetic flow meter
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K21 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K50..K62 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1,2,3,4 Wire terminals 2.5mm2
Complete
14.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah - pcs 2
All mounted in the ROMTK cabinet Complete
14.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
14.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for inlet and outlet pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors and limit pressure switches.
14.13 | Supply, delivery and installation of limit pressure detector |  | pcs | 2
Electric contact manometer with two adjustable limit switches, used for alarming, type Teleoptik or equivalent
Measuring range : 0-16 bar
Fitting: 0.5 inch
14.14 | Supply, delivery and installation of absolute pressure transmitters |  | pcs | 2
Compact version
CHARACTERISTICS
• Available ranges (0... 10 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
14.15 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
14.16 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND250 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
14.17 | Delivery, installation and commissioning of an electromagnetic flow meter Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics Nominal diameters DN 250 Hard rubber or polyurethane lining High accuracy: ± 0.5% (option: ± 0.2%) Robust field housing, IP 67 wall-mount housing for straightforward Class 0.30 Linearity 0.1 Repeatability 0.1 Power supply: 24VDC ; power consumption: <5W Display: 122x32 dots LCD graphical display with backlight Configuring: numerical via keypad, range, measurement unit,sensitivity etc. Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Switch outputs: pulse for external totalizer, 0.1A, 250V photorelay configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay Sensor input: type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit oversampling: x100 ; sensitivity:0.1 uV Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit Ambient temperature: -20…+70 0C Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK |  | set | 2
14.18 | Supply, delivery, installation and wiring of a conductive level detector valve chamber flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
14.19 | Cable delivery, installation and connecting |  | set | 1
Delivery and installation of power cables inside MRS for interior lighting and socket supply. Cables are to be installed out-of-walls using clamps.
Cable installation also includes cable end preparation and labelling, cable connecting and/or splicing and junction boxes installation.
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00Y 3x2.5 10 Power supply 220VAC, 50Hz
W01 PP00Y 3x2.5 20 Flow meter supply 220VAC
W02 PP00Y 3x2.5 20 Flow meter supply 220VAC
W03 IyStY 15x2x0.6 10 ROMTK to GRO
W04 IyStY 1x2x0.6 20 To flooding detector probes
W05 IyStY 1x2x0.6 40 Open door detector
W06 IyStY 2x2x0.6 30 Isolation valve SV1 limit switch
W07 IyStY 2x2x0.6 30 Isolation valve SV2 limit switch
W08 IyStY 2x2x0.6 30 Isolation valve SV3 limit switch
W09 IyStY 2x2x0.6 30 Isolation valve SV4 limit switch
W10 IyStY 2x2x0.6 25 Inlet limit pressure detector
W11 IyStY 2x2x0.6 25 Outlet limit pressure detector
W12 LiYCy 2x0.75 25 To inlet pressure sensor
W13 LiYCy 2x0.75 25 To outlet pressure sensor
W14 LiYCy 2x0.75 25 To line 1 flow meter
W15 LiYCy 2x0.75 25 To line 2 flow meter
W16 LiYCy 4x0.75 25 To V1 position transducer
W17 LiYCy 4x0.75 25 To V2 position transducer
W100 LiYCy 8x0.6 2 Comm. cable, PLC-T96SR
W101 Antenna cable
14.20 | Electrical installation services |  | set | 1
The separate distribution cabinet with power inlet and power meter unit is assumed to be installed by authorised EPS personal (EPS stands for Public Enterprise ”Electric power industry of Serbia”).
Setting and tightening of electric installation accessories in the MRS, i.e. junction boxes, switches and lights. Connecting and functional testing.
Accessories:
Single-phase switch 220VAC 10A, in silumin case pcs 3 Single phase out-of-wall power socket (receptacle) 16A pcs 2 Three phase out-of-wall power socket 16A pcs 1
Flat type deck lighting fixture with incandescent bulb 200W, IP55, type BRODSKA or equivalent pcs 3
Other unspecified accessories and works
Complete.
14 | MRS CICEVAC - TOTAL | Sub-total carried to Summary II
15 | SOFTWARE SUPPORT
15.1 | The application software for the monitoring stations in CCC1 Lipovac, CCC2 Direkcija, CCC3 Majdevo and CCC4 Ćelije, which means configuration of additional a. variables - tags, b. mimic diagrams, c. reports, d. operator interfaces that concerns all five metering and regulation stations. |  | set | 1
The application software for the main server in CCC1 Lipovac, which means configuration of communication and control capabilities concerning all five MRSs.
15.2 | The Master PLC-1.1 application software, which means additional communicational and control features necessary for integration of all five MRSs into the CCMS. |  | set | 1
15.3 | The application software for communication centres: PLC-1.7, PLC-3.8 and PLC5.23, which means implementing of additional communication capabilities concerning reliable data transfer with all five MRSs. |  | set | 1
15 | SOFTWARE SUPPORT - TOTAL | Sub-total carried to Summary II
16 | AS-BUILT DOCUMENTATION
16.1 | The production and assembly of as-built documentation KS DP09 |  | set | 1
for the monitoring and regulation stations MRS.
16 | AS-BUILT DOCUMENTATION - TOTAL | Sub-total carried to Summary II
17 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
17.1 | Parameter adjustment and putting into operation communication links between authorised communication centres and metering anrd regulation stations. Radio communication and data transfer testing. |  | set | 1
Parameter adjustment, testing and putting into operation measuring equipment, automation systems and remote controls.
Commissioning and performance verification
Putting into trial operation
The trial operation will last 15 days
17 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION - TOTAL | Sub-total carried to Summary II
SUMMARY II.
II | METERING AND REGULATION STATIONS |  |  |  |  | Amount (euro)
10 | MRS LIPOVAC
11 | MRS KRUŠEVAC (MAKREŠANE)
12 | MRS STALAĆ
13 | MRS VARVARIN
14 | MRS ĆIĆEVAC
15 | SOFTWARE SUPPORT
16 | AS-BUILT DOCUMENTATION
17 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
II | THE METERING AND REGULATION STATIONS | TOTAL carried to Summary A.
III | RESERVOIRS - "REGIONAL SYSTEM"
18 | RESERVOIR R LIPOVAC
18.1 | Supply, delivery and wiring of the PLC-1.6, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
18.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
18.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
18.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
18.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
18.6 | The PLC-1.6 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests coming from the authorised communication centre PLC-3.8,
c. diagnostic functions for measuring equipment and the PLC itself.
18.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
18.8 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Reservoir level sensor CS600
U6 Reservoir level sensor CS600
U7 Radio-modem T-96SR
U8 Over voltage protection FRD24 HF
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection VF230
U12 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relay 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relay 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
18.9 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
18.10 | Supply. delivery and installation of residual chlorine analyser, type Depolox or equivalent |  | set | 1
The analyser contains:
A) Depolox basic module
analogue current output 4-20 mA
B) Depolox wall mounted sensor
conductivity > 300mS
C) Accessories:
mounting accessories
D) Sampling pump
Testing and putting into operation.
18.11 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 2
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
19.12 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
18.13 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
18.14 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
18.15 | Supply, delivery and installation of the mounting brackets |  | pcs | 2
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
18.16 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W02 IyStY 4x2x0.6 20 To level probes, chamber 1
W03 IyStY 4x2x0.6 20 To level probes, chamber 2
W04 IyStY 1x2x0.6 30 Open door detector
W05 LiYCy 5x0.75 20 To level sensor, chamber 1
W06 LiYCy 5x0.75 20 To level sensor, chamber 2
W07 LiYCy 5x0.75 20 To residual clorine analyser
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
18 | RESERVOIR R LIPOVAC - TOTAL | Sub-total carried to Summary III
20 | RESERVOIR R BAGDALA
20.1 | Supply, delivery and connecting of an additional module for the existing PLC-1.7, type CJ1M-CPU12: |  | set | 1
Ethernet module CJ1W-ETN21 pcs 1
Existing modules:
CJ1W-PD025
CJ1M-CPU12
CJ1W-SCU41
CJ1W-ID211 NL
CJ1W-OD212
CJ1W-AD081-V1 NL
CJ1W-AD041-V1 NL
20.2 | Upgrade of the PLC-1.7 application software |  | set | 1
Retaining all acquisition, control and diagnostic functions of the existing PLC-1.7 software, upgrade its communication functions so that the following is provided:
o regular polling of all the communication slaves in a radio-modem network every 30s,
o buffering the most recently obtained data from the slaves, together with IO signals obtained directly through its own IO modules,
o sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL,
o sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request,
o reception of command messages from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network, with higher priority than regular polls,
o sending an extra poll to the slave previously targeted by a command, to provide prompt command execution status,
o sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL.
20.3 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Terminal unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width: 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used: IP V4, UDP, TCP, IC MP, Telnet, HTTP, FTP, SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Wind resistance 190 km/hr
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation.To be delivered with clamps for radio unit and reflector pcs 1
Radio-device power supply, 90-220VAC/24VDC, min 0,3 A, indoor construction, with Ethernet by-pass pcs 1
Ethernet Surge Suppressor , for outdoor installation pcs 1
FTP cable cat.5e, patch, 30m pcs 1
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Radio-device and control module outdoor installation pcs 1
Set-up and configuration of radio-device and control module pcs 1
Unspecified consumables pcs 1
Travel and accommodation expenses pcs 1
System commissioning pcs 1
Unspecified material pcs 1
20.4 | LAN Ethernet 10/100 BaseT installation, including the following: Ethernet Switch L2, UTP cable 30m, surge protection devices, wiring ducts |  | set | 1
Active and passive LAN equipment
20.5 | Supply. delivery and installation of residual chlorine analyser, type Depolox or equivalent |  | set | 1
The analyser contains:
A) Depolox basic module
analogue current output 4-20 mA
B) Depolox wall mounted sensor
conductivity > 300mS
C) Accessories:
mounting accessories
D) Sampling pump
Testing and putting into operation.
20.6 | Delivery, installation and commissioning of an electromagnetic flow meter, |  | set | 1
DN80 NP16, intended for PS Bagdala outlet towards storage reservoir R Šumice
Electromagnetic flow meter with display and current loop output, similar to type: IC720 with the following characteristics
Nominal diameters DN 80
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
20.7 | Reconfiguration of the existing radio-communication equipment T96SR |  | set | 1
Radio-modem frequency adjustment in accordance with the new communication functions of this location.
20 | RESERVOIR R BAGDALA - TOTAL | Sub-total carried to Summary III
21 | RESERVOIR R TODOROVA KULA
21.1 | Supply, delivery and wiring of the PLC-1.14, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
21.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
21.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
21.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
21.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
21.6 | The PLC-1.14 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests coming from the authorised communication centre PLC-5.23,
c. diagnostic functions for measuring equipment and the PLC itself.
21.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
21.8 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Reservoir level sensor CS600
U6 Reservoir level sensor CS600
U7 Radio-modem T-96SR
U8 Over voltage protection FRD24 HF
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection VF230
U12 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
21.9 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
21.10 | Supply. delivery and installation of residual chlorine analyser, type Depolox or equivalent |  | set | 1
The analyser contains:
A) Depolox basic module
analogue current output 4-20 mA
B) Depolox wall mounted sensor
conductivity > 300mS
C) Accessories:
mounting accessories
D) Sampling pump
Testing and putting into operation.
21.11 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 2
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
21.12 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
21.13 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
21.14 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
21.15 | Supply, delivery and installation of the mounting brackets |  | pcs | 2
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
21.16 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W02 IyStY 4x2x0.6 20 To level probes, chamber 1
W03 IyStY 4x2x0.6 20 To level probes, chamber 2
W04 IyStY 1x2x0.6 30 Open door detector
W05 LiYCy 5x0.75 20 To level sensor, chamber 1
W06 LiYCy 5x0.75 20 o level sensor, chamber 2
W07 LiYCy 5x0.75 20 To residual clorine analyser
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
21 | RESERVOIR R TODOROVA KULA - TOTAL | Sub-total carried to Summary III
22 | RESERVOIR R VARVARIN
22.1 | Supply, delivery and wiring of the PLC-1.15, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
22.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
22.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
22.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
22.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
22.6 | The PLC-1.15 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests coming from the authorised communication centre PLC-5.23,
c. diagnostic functions for measuring equipment and the PLC itself.
22.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
22.8 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Reservoir level sensor CS600
U6 Reservoir level sensor CS600
U7 Radio-modem T-96SR
U8 Over voltage protection FRD24 HF
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection VF230
U12 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
22.9 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
22.10 | Supply. delivery and installation of residual chlorine analyser, type Depolox or equivalent |  | set | 1
The analyser contains:
A) Depolox basic module
analogue current output 4-20 mA
B) Depolox wall mounted sensor
conductivity > 300mS
C) Accessories:
mounting accessories
D) Sampling pump
Testing and putting into operation.
22.11 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 2
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
22.12 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
22.13 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
22.14 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
22.15 | Supply, delivery and installation of the mounting brackets |  | pcs | 2
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
22.16 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W02 IyStY 4x2x0.6 20 To level probes, chamber 1
W03 IyStY 4x2x0.6 20 To level probes, chamber 2
W04 IyStY 1x2x0.6 30 Open door detector
W05 LiYCy 5x0.75 20 To level sensor, chamber 1
W06 LiYCy 5x0.75 20 To level sensor, chamber 2
W07 LiYCy 5x0.75 20 To residual clorine analyser
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
22 | RESERVOIR R VARVARIN - TOTAL | Sub-total carried to Summary III
23 | RESERVOIR R CICEVAC
23.1 | Supply, delivery and wiring of the PLC-1.16, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
23.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
23.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
23.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
23.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
23.6 | The PLC-1.16 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests coming from the authorised communication centre PLC-5.23,
c. diagnostic functions for measuring equipment and the PLC itself.
23.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
23.8 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Reservoir level sensor CS600
U6 Reservoir level sensor CS600
U7 Radio-modem T-96SR
U8 Over voltage protection FRD24 HF
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection VF230
U12 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
23.9 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
23.10 | Supply. delivery and installation of residual chlorine analyser, type Depolox or equivalent |  | set | 1
The analyser contains:
A) Depolox basic module
analogue current output 4-20 mA
B) Depolox wall mounted sensor
conductivity > 300mS
C) Accessories:
mounting accessories
D) Sampling pump
Testing and putting into operation.
23.11 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 2
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
23.12 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
23.13 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
23.14 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
23.15 | Supply, delivery and installation of the mounting brackets |  | pcs | 2
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
23.16 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W02 IyStY 4x2x0.6 20 To level probes, chamber 1
W03 IyStY 4x2x0.6 20 To level probes, chamber 2
W04 IyStY 1x2x0.6 30 Open door detector
W05 LiYCy 5x0.75 20 To level sensor, chamber 1
W06 LiYCy 5x0.75 20 To level sensor, chamber 2
W07 LiYCy 5x0.75 20 To residual clorine analyser
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
23 | RESERVOIR R CICEVAC - TOTAL | Sub-total carried to Summary III
24 | SOFTWARE SUPPORT
24.1 | The application software for the monitoring stations in CCC1 Lipovac, CCC2 Direkcija, CCC3 Majdevo and CCC4 Ćelije, which means configuration of additional a. variables - tags, b. mimic diagrams, c. reports, d. operator interfaces that concerns all five storage reservoirs within "The Regional System". |  | set | 1
The application software for the main server in CCC1 Lipovac, which means configuration of communication and control capabilities concerning all five reservoirs within "The Regional System"
24.2 | The Master PLC-1.1 application software, which means additional communicational and control features necessary for integration of all five reservoirs within "The Regional System" into the CCMS. |  | set | 1
24.3 | The application software for communication centres: PLC-3.8 and PLC5.23, which means implementing of additional communication capabilities concerning reliable data transfer with all five storage reservoirs within "The Regional System". |  | set | 1
24 | SOFTWARE SUPPORT - TOTAL | Sub-total carried to Summary III
25 | AS-BUILT DOCUMENTATION
25.1 | The production and assembly of as-built documentation KS DP09 |  | set | 1
for the storage reservoirs within "The Regional System"
25 | AS-BUILT DOCUMENTATION - TOTAL | Sub-total carried to Summary III
26 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
26.1 | Parameter adjustment and putting into operation communication links between authorised communication centres and five storage reservoirs within "The Regional System". Radio communication and data transfer testing. |  | set | 1
Parameter adjustment, testing and putting into operation measuring equipment, automation systems and remote controls.
Commissioning and performance verification
Putting into trial operation
The trial operation will last 15 days
26 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION - TOTAL | Sub-total carried to Summary III
SUMMARY III.
III | RESERVOIRS - "REGIONAL SYSTEM" |  |  |  |  | Amount (euro)
18 | RESERVOIR R LIPOVAC
20 | RESERVOIR R BAGDALA
21 | RESERVOIR R TODOROVA KULA
22 | RESERVOIR R VARVARIN
23 | RESERVOIR R CICEVAC
24 | SOFTWARE SUPPORT
25 | AS-BUILT DOCUMENTATION
26 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
III | RESERVOIRS - "REGIONAL SYSTEM" | TOTAL carried to Summary A.
IV | CHLORINATION STATION
As a part of HS design and construction, a "dry" room with a separate entrance will be built within the object, intended for accommodation of the CCMS cabinet, the main distribution cabinet with power meter unit and chlorine residual analyser. The overall room dimensions should be: width 1.5-2m, length 2m.
The entire object is to be constructed under a single flat roof, in compliance with the construction requirements and the original design.
Interior power and lighting distribution installation will be incorporated into a separate Bill of Materials within the construction Design Documents. The same applies for the electric service obtaining.
28 | THE CHLORINATION STATION HS LIPOVAC
28.1 | Supply, delivery and wiring of the PLC-1.17, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OD212 pcs 1
CJ1W-AD041-V1 NL pcs 1
CJ1W-DA021-V1 NL pcs 1
28.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
28.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
28.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
28.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
28.6 | The PLC-1.17 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests and command messages coming from the authorised communication centre PLC-3.8,
c. transferring start/stop commands and chlorine dosage set point, obtained form the authorized command and control centre, to autonomous chlorinator, if applicable,
d. diagnostic functions for measuring equipment and the PLC itself.
28.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
28.8 | Reconstruction of the main distribution cabinet, in order to provide power supply for the CCMS distribution cabinet. |  | set | 1
Installation of an appropriate two-pole circuit breaker 220VAC, 10A, and wire terminals in order to provide AC power to ROMTK.
28.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical ROMTK connection diagram.
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1xOD212, 1XAD041-v1, 1xDA021-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display DP3, for pressure indication
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K16 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K51 Single pole interface relay 24VDC, G2RV-SLC700 DC24
28.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
28.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 1
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
28.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of a pressure sensor.
28.13 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 1
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
28.14 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
28.15 | Supply, delivery, installation and wiring of a conductive level detector HS flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
28.16 | Supply, delivery and installation of the mounting brackets |  | set | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
28.17 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 10 Power supply of ROMTK
W01 IyStY 5x2x0.8 20 From ROMTK to the chlorinator
W02 IyStY 3x2x0.8 20 Level probes, flooding detector
W03 IyStY 1x2x0.6 20 Open door detectors
W04 LiYCy 2x0.75 20 Pressure sensor
W05 LiYCy 2x0.75 20 Chlorinator, flow meter signal
W06 LiYCy 2x0.75 20 Chlorinator, chlorine dosage
W07 LiYCy 2x0.75 20 Chlorinator, chlorine residual
W08 LiYCy 2x0.75 20 Chlorinator, settings
W100 LiYCy 4x2x0.6 2 Comm, PLC to radio-modem
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
28 | CHLORINATION STATION HS LIPOVAC - TOTAL | Sub-total carried to Summary IV
29 | SOFTWARE SUPPORT
29.1 | The application software for the monitoring stations in CCC1 Lipovac, CCC2 Direkcija, CCC3 Majdevo and CCC4 Ćelije, which means configuration of additional a. variables - tags, b. mimic diagrams, c. reports, d. operator interfaces that concerns HS Lipovac. |  | set | 1
The application software for the main server in CCC1 Lipovac, which means configuration of communication and control capabilities concerning HS Lipovac.
29.2 | The Master PLC-1.1 application software, which means additional communicational and control features necessary for integration of HS Lipovac into the CCMS. |  | set | 1
29.3 | The application software for communication centre PLC-3.8, which means implementing of additional communication capabilities concerning reliable data transfer with HS Lipovac. |  | set | 1
29 | SOFTWARE SUPPORT - TOTAL | Sub-total carried to Summary IV
30 | AS-BUILT DOCUMENTATION
30.1 | The production and assembly of as-built documentation KS DP09 |  | set | 1
for the HS Lipovac.
30 | AS-BUILT DOCUMENTATION - TOTAL | Sub-total carried to Summary IV
31 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
31.1 | Parameter adjustment and putting into operation the communication link between authorised communication centre and HS Lipovac. Radio communication and data transfer testing. |  | set | 1
Parameter adjustment, testing and putting into operation measuring equipment and remote controls.
Commissioning and performance verification
Putting into trial operation
The trial operation will last 15 days
31 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION - TOTAL | Sub-total carried to Summary IV
SUMMARY IV.
IV | CHLORINATION STATION |  |  |  |  | Amount (euro)
28 | CHLORINATION STATION HS LIPOVAC
29 | SOFTWARE SUPPORT
30 | AS-BUILT DOCUMENTATION
31 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
IV | CHLORINATION STATION | TOTAL carried to Summary A.
A. | SUMMARY A - SUBSYSTEM „REGIONAL SYSTEM“ |  |  |  |  | Amount (euro)
I | COMMAND AND CONTROL CENTRES
II | METERING AND REGULATION STATIONS
III | RESERVOIRS - "REGIONAL SYSTEM"
IV | CHLORINATION STATION
A. | SUBSYSTEM „REGIONAL SYSTEM“ | TOTAL carried to Bill No.9
B. | SUBSYSTEM “SYSTEM EAST”
1 | PUMPING STATION PS GAGLOVO 2
1.1 | Supply, delivery and wiring of the PLC-3.7, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
1.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
1.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
1.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
1.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
1.6 | The PLC-3.7 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. communication services to client data requests and command messages, coming from the authorised communication centre PLC-3.8,
e. diagnostic functions for measuring equipment and the PLC itself.
1.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
1.8 | Reconstruction of an existing motor control cabinet ROP, which means: |  | set | 1
o redesign and reconstruction of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,
o installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,
o installation of auxiliary contacts, relays and wire terminals in order to connect the motor control cabinet to the CCMS cabinet,
1.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the pumping station.
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in pumping stations (PS).
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Flow meter transducer IC720
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2,S3,S4 Three-pole switch 20A/1-0-2/3P/V M10HEU3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC, PGR3131,2P,230VAC/12A
K8...K10 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K11 Single pole interface relay 24VDC, G2RV-SLC700 DC24
X1,2,3 Wire terminals 2.5 mm2
1.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
1.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
1.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors.
1.13 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
1.14 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
1.15 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND80 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
1.16 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the outlet of PS Gaglovo 2
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 80
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
1.17 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
1.18 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
1.19 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00-Y 3x2.5 10 Power supply 220VAC, 50Hz
W02 IyStY 8x2x0.6 10 ROMTK to ROP
W03 IyStY 1x2x0.6 20 To flooding detector probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 2x0.75 15 To inlet pressure sensor
W06 LiYCy 2x0.75 15 To outlet pressure sensor
W07 LiYCy 3x0.75 20 To outlet flow meter sensor
W08 LiYCy 2x0.75 20 To outlet flow meter sensor
W100 LiYCy 8x0.6 2 Comm, PLC-T96SR, RS232
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
1.20 | Construction works |  | set | 1
Construct a metal platform annex inside the PS, lengthen from the doorway along the right side wall, 1m wide and properly supported, in order to provide accommodation and access to the distribution cabinets ROMTK.
1 | PUMPING STATION PS GAGLOVO 2 - TOTAL | Sub-total carried to Summary B
2 | HYDRO PRESS AND RESERVOIR HPR MALI SILJEGOVAC
2.1 | Supply, delivery and wiring of the PLC-3.8, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU12 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
CJ1W-DA021-V1 NL pcs 1
CJ1W-ETN21 pcs 1
2.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
2.3 | Supply and delivery of an aerial |  | set | 1
Omnidirectional antenna:
Frequency range: 390-520MHz
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
2.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
2.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
2.6 | The PLC-3.8 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. diagnostic functions for measuring equipment and the PLC itself,
e. a set of communication functions:
o regular polling of all the communication slaves in a radio-modem network every 30s,
o buffering the most recently obtained data from the slaves, together with IO signals obtained directly through its own IO modules,
o sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL,
o sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request,
o reception of commans from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network, with higher priority than regular polls,
o sending an extra poll to the slave previously targeted by a command, to provide prompt command execution status,
o sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL.
2.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
2.8 | Reconstruction of an existing motor control cabinet ROP, which means: |  | set | 1
o installation of one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,
o redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,
o installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet,
2.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the hydro press object.
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in HPR facilities.
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
U15 Level detector DN2
U17 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2 Three-pole switch 20A/1-0-2/3P/V M10HEU3
S3,S4 Three-pole switch 20A/1-0/3P/V M10HEA3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC, PGR3131,2P,230VAC/12A
K8 Single pole interface relay 220VAC, G2RV-SLC700 AC230
K9 Two pole interface relay 220VAC, PGR3131,2P,230VAC/12A
K10...13 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1,2,3,4 Wire terminals 2.5 mm2
2.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
2.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
2.12 | Supply, delivery and installation of limit pressure detector |  | pcs | 1
Electric contact manometer with two adjustable limit switches, used for alarming, type Teleoptik or equivalent
Measuring range : 0-16 bar
Fitting: 0.5 inch
2.13 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of a pressure sensor and a limit pressure switch.
2.14 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 1
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
2.15 | Supply, delivery and installation of residual chlorine analyser, type Depolox or equivalent |  | set | 1
The analyser contains:
A) Depolox basic module
analogue current output 4-20 mA
B) Depolox wall mounted sensor
conductivity > 300mS
C) Accessories:
mounting accessories
D) Sampling pump
Testing and putting into operation.
2.16 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
2.17 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Terminal unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width: 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used: IP V4, UDP, TCP, IC MP, Telnet, HTTP, FTP, SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Wind resistance 190 km/hr
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 1
Radio-device power supply, 90-220VAC/24VDC, min 0,3 A, indoor construction, with Ethernet by-pass pcs 1
Ethernet Surge Suppressor , for outdoor installation pcs 1
FTP cable cat.5e, patch, 30m pcs 1
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Radio-device and control module outdoor installation pcs 1
Set-up and configuration of radio-device and control module pcs 1
unspecified consumables pcs 1
Travel and accommodation expenses pcs 1
System commissioning pcs 1
Unspecified material pcs 1
2.18 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
2.19 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
2.20 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
2.21 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
2.22 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
2.23 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz,
W02 IyStY 8x2x0.6 10 ROMTK to ROP, 220VAC
W03 IyStY 4x2x0.6 30 To reservoir level probes
W04 IyStY 1x2x0.6 15 To flooding detector probes
W05 IyStY 1x2x0.6 40 Open door detector, 24VDC
W06 IyStY 1x2x0.6 15 Low outlet pressure detector
W07 IyStY 1x2x0.6 15 High outlet pressure detector
W08 LiYCy 2x0.75 15 To inlet pressure sensor
W09 LiYCy 3x0.75 15 To outlet pressure sensor
W10 LiYCy 5x0.75 30 To reservoir level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
Cable routing from the storage reservoir to the hydro press object, trench excavation, cables laying and reinstatement, total distance 15m.
2.24 | Construction works |  | set | 1
Construct a metal platform annex inside the HPR, lengthen to the left from doorway, along the front wall to the left side wall, 1m wide and properly supported, in order to provide accommodation and access to the distribution cabinets ROMTK and ROP (if moved).
2 | HYDRO PRESS AND RESERVOIR HPR MALI SILJEGOVAC - TOTAL | Sub-total carried to Summary B
3 | SOFTWARE SUPPORT
3.1 | The application software for the monitoring stations in CCC1 Lipovac and CCC2 Direkcija, which means configuration of additional a. variables - tags, b. mimic diagrams, c. reports, d. operator interfaces that concerns the objects within distribution network DN Gaglovo 2. |  | set | 1
The application software for the main server in CCC1 Lipovac, which means configuration of communication and control capabilities concerning DN Gaglovo 2.
3.2 | The Master PLC-1.1 application software, which means additional communicational and control features necessary for integration of DN Gaglovo 2 into the CCMS. |  | set | 1
3 | SOFTWARE SUPPORT - TOTAL | Sub-total carried to Summary B
4 | AS-BUILT DOCUMENTATION
4.1 | The production and assembly of as-built documentation KS DP09 |  | set | 1
for the distribution network DN Gaglovo 2.
4 | AS-BUILT DOCUMENTATION - TOTAL | Sub-total carried to Summary B
5 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
5.1 | Parameter adjustment and putting into operation the communication links between authorised communication centre and all the objects within DN Gaglovo 2. Radio communication and data transfer testing. |  | set | 1
Parameter adjustment, testing and putting into operation measuring equipment, especially residual chlorine analyser, automation systems, remote pump and frequency invertor control.
Commissioning and performance verification
Putting into trial operation
The trial operation will last 15 days
5 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION - TOTAL | Sub-total carried to Summary B
B | SUMMARY B - SUBSYSTEM “SYSTEM EAST” |  |  |  |  | Amount (euro)
1 | PUMPING STATION PS GAGLOVO 2
2 | HYDRO PRESS AND RESERVOIR HPR MALI SILJEGOVAC
3 | SOFTWARE SUPPORT
4 | AS-BUILT DOCUMENTATION
5 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
B. | SUBSYSTEM “SYSTEM EAST” | TOTAL carried to Bill No. 9
C. | SUBSYSTEM “RASINA WALLY SYSTEM”
I | DISTRIBUTION NETWORK DN NAUPARE
1 | PUMPING STATION PS NAUPARE 1
1.1 | Supply, delivery and wiring of the PLC-4.20, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
1.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
1.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
1.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
1.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
1.6 | The PLC-4.20 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. communication services to client data requests and command messages, coming from the authorised communication centre PLC-4.12,
e. diagnostic functions for measuring equipment and the PLC itself.
1.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
1.8 | Reconstruction of an existing motor control cabinet ROP, which means: |  | set | 1
o removal of the GSM device output relay contact from a motor control circuitry,
o installation of one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,
o installation of two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,
o auxiliary relays for motor command circuitry reconstruction, providing normal PS operation both in previously existing local or recently introduced remote modes,
o redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,
o installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,
o installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet,
Dismantle the existing control cabinet with the GSM device.
1.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in pumping stations (PS).
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Flow meter transducer IC720
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2,S3,S4 Three-pole switch 20A/1-0-2/3P/V M10HEU3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC: PGR3131,2P,230VAC/12A
K8...K10 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K11 Single pole interface relay 24VDC, G2RV-SLC700 DC24
X1,2,3 Wire terminals 2.5 mm2
1.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
1.11 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Central access unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used IP V4, UDP, TCP , IC MP, Telnet, HTTP , FTP , SN MP
Network Management HTTP , TELN ET, FTP , SN MP Version 2c
Wind resistance 190 km/hr
Temperature range: -40°C to +55°C
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Point-to-point unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip. Allowed passive reflector to be added
Antenna Beam Width 3 dB internal antenna beam width 60deg. Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used: IP V4, UDP, TCP, IC MP, Telnet, HTTP, FTP, SN MP
Network Management HTTP , TELN ET, FTP , SN MP Version 2c
Wind resistance 190 km/hr
Point -to-Point devices, can be with passive reflectors, with minimal requirements:
Signalling Rate: min.10 Mbps
Aggregate Throughput: min.7.5 Mbps
Typical LoS Range 56 km with passive reflector
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 1
Radio-device power supply , 90-220VAC/24VDC, min 0,3 A, indoor construction, with Ethernet by-pass pcs 2
Ethernet Surge Suppressor , for outdoor installation pcs 2
FTP cable cat.5e, patch, 30m pcs 2
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Radio-device and control module outdoor installation pcs 2
Set-up and configuration of radio-device and control module pcs 2
Unspecified consumables pcs 1
1.12 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
1.13 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors.
1.14 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
1.15 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
1.16 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND80 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
1.17 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the outlet of PS Naupare 1
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 80
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
1.18 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
1.19 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
1.20 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00-Y 3x2.5 10 Power supply 220VAC, 50Hz
W02 IyStY 8x2x0.6 10 ROMTK to ROP
W03 IyStY 1x2x0.6 20 To flooding detector probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 2x0.75 15 To inlet pressure sensor
W06 LiYCy 2x0.75 15 To outlet pressure sensor
W07 LiYCy 3x0.75 20 To outlet flow meter sensor
W08 LiYCy 2x0.75 20 To outlet flow meter sensor
W100 LiYCy 8x0.6 2 Comm, PLC-T96SR, RS232
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
1.21 | Construction works |  | set | 1
Construct a metal platform annex inside the PS, lengthen to the left from doorway, along the front wall to the left side wall, 1m wide and properly supported, in order to provide accommodation and access to the distribution cabinets ROMTK and ROP (if moved).
1 | PUMPING STATION PS NAUPARE 1 - TOTAL | Sub-total carried to Summary I
2 | RESERVOIR R NAUPARE 1
2.1 | Supply, delivery and wiring of the PLC-4.21, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
2.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
2.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
2.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
2.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
2.6 | The PLC-4.21 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests, coming from the authorised communication centre PLC-4.12,
c. diagnostic functions for measuring equipment and the PLC itself.
2.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
2.8 | Reconstruction of the main distribution cabinet RO, |  | set | 1
which means installation of:
o F1, F2 two circuit breakers PGR4470, SI C10/2, intended for power supply of the separate CCMS cabinet ROMTK,
o DIN Rail Mounting Terminal Blocks-Clamps, 600V/25A rated, for stranded wire up to 2.5mm2 or solid wire up to 4mm2,
o various accessories: cable lugs, cable end sleeves, stranded isolated wire 1.5mm2 and 2.5mm2, heat shrink tubing, cable tags, device identification marks etc.
Reconstruction includes delivery, connecting and labelling of a cable PP00 3x2.5mm2 for the ROMTK power supply from the distribution cabinet RO.
The scope of works also includes removal of the existing GSM device and its wiring.
2.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
2.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
2.11 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
2.12 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
2.13 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
2.14 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
2.15 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
2.16 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W03 IyStY 4x2x0.6 20 To storage level probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 5x0.75 20 To storage level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
2.17 | Electric power service obtaining |  | set | 1
Works and procedures necessary for electric power service providing: service request submission for 10.5kW, obtaining required approvals and permits, cable 4x35mm2 routing from the distribution network approx. 100m away, trench excavation and cable laying, power meter installation. Also includes all other works and taxes required by authorised power distribution company in order to obtain electric power service.
2 | RESERVOIR R NAUPARE 1 - TOTAL | Sub-total carried to Summary I
3 | PUMPING STATION PS NAUPARE 2
3.1 | Supply, delivery and wiring of the PLC-4.22, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
3.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
3.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
3.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
3.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate.
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
3.6 | The PLC-4.22 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. communication services to client data requests and command messages, coming from the authorised communication centre PLC-4.12,
e. diagnostic functions for measuring equipment and the PLC itself.
3.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
3.8 | Reconstruction of an existing motor control cabinet ROP, which means: |  | set | 1
o installation of one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,
o installation of two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,
o auxiliary relays for motor command circuitry reconstruction, providing normal PS operation both in previously existing local or recently introduced remote modes,
o redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,
o installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,
o installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet,
3.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in pumping stations (PS).
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Flow meter transducer IC720
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2,S3,S4 Three-pole switch 20A/1-0-2/3P/V M10HEU3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC: PGR3131,2P,230VAC/12A
K8...K10 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K11 Single pole interface relay 24VDC, G2RV-SLC700 DC24
X1,2,3 Wire terminals 2.5 mm2
3.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
3.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
3.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors.
3.13 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
3.14 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
3.15 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND80 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
3.16 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the outlet of PS Naupare 2
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 80
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
3.17 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
3.18 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
3.19 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00-Y 3x2.5 10 Power supply 220VAC, 50Hz
W02 IyStY 8x2x0.6 10 ROMTK to ROP
W03 IyStY 1x2x0.6 20 To flooding detector probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 2x0.75 15 To inlet pressure sensor
W06 LiYCy 2x0.75 15 To outlet pressure sensor
W07 LiYCy 3x0.75 20 To outlet flow meter sensor
W08 LiYCy 2x0.75 20 To outlet flow meter sensor
W100 LiYCy 8x0.6 2 Comm, PLC-T96SR, RS232
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
3.20 | Construction works |  | set | 1
Construct a metal platform annex inside the PS, lengthen to the left from doorway, along the front wall to the left side wall, 1m wide and properly supported, in order to provide accommodation and access to the distribution cabinets ROMTK and ROP (if moved).
3 | PUMPING STATION PS NAUPARE 2 - TOTAL | Sub-total carried to Summary I
4 | RESERVOIR R NAUPARE 2
4.1 | Supply, delivery and wiring of the PLC-4.23, type CJ1M or adequate |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
4.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
4.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
4.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
4.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
4.6 | The PLC-4.23 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests, coming from the authorised communication centre PLC-4.12,
c. diagnostic functions for measuring equipment and the PLC itself.
4.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
4.8 | Reconstruction of the main distribution cabinet RO, |  | set | 1
which means installation of:
o F1, F2 two circuit breakers PGR4470, SI C10/2, intended for power supply of the separate CCMS cabinet ROMTK,
o DIN Rail Mounting Terminal Blocks-Clamps, 600V/25A rated, for stranded wire up to 2.5mm2 or solid wire up to 4mm2,
o various accessories: cable lugs, cable end sleeves, stranded isolated wire 1.5mm2 and 2.5mm2, heat shrink tubing, cable tags, device identification marks etc.
Reconstruction includes delivery, connecting and labelling of a cable PP00 3x2.5mm2 for the ROMTK power supply from the distribution cabinet RO.
4.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
4.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
4.11 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
4.12 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
4.13 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
4.14 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
4.15 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
4.16 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W03 IyStY 4x2x0.6 20 To storage level probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 5x0.75 20 To storage level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
4.17 | Electric power service obtaining |  | set | 1
Works and procedures necessary for electric power service providing: service request submission for 10.5kW, obtaining required approvals and permits, cable 4x35mm2 routing from the distribution network approx. 300m away, reinforced concrete utility poles installation, gas discharge surge protectors and power meter installation. Also includes all other works and taxes required by authorised power distribution company in order to obtain electric power service.
4 | RESERVOIR R NAUPARE 2 - TOTAL | Sub-total carried to Summary I
5 | SOFTWARE SUPPORT
5.1 | The application software for the monitoring stations in CCC1 Lipovac and CCC2 Direkcija, which means configuration of additional a. variables - tags, b. mimic diagrams, c. reports, d. operator interfaces that concerns DN Naupare. |  | set | 1
The application software for the main server in CCC1 Lipovac, which means configuration of communication and control capabilities concerning DN Naupare.
5.2 | The Master PLC-1.1 application software, which means additional communicational and control features necessary for integration of DN Naupare into the CCMS. |  | set | 1
5.3 | The application software for communication centre PLC-4.12, which means implementing of additional communication capabilities concerning locations within DN Naupare. |  | set | 1
5 | SOFTWARE SUPPORT - TOTAL | Sub-total carried to Summary I
6 | AS-BUILT DOCUMENTATION PRODUCTION
6.1 | The production and assembly of as-built documentation KS DP09 |  | set | 1
for the distribution network DN Naupare.
6 | AS-BUILT DOCUMENTATION PRODUCTION - TOTAL | Sub-total carried to Summary I
7 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
7.1 | Parameter adjustment and putting into operation communication links between the authorised communication centre and all the objects within DN Naupare. Radio communication and data transfer testing. |  | set | 1
Parameter adjustment, testing and putting into operation measuring equipment, automation systems and remote controls.
Commissioning and performance verification
Putting into trial operation
The trial operation will last 15 days
7 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION - TOTAL | Sub-total carried to Summary I
I | SUMMARY I. - DISTRIBUTION NETWORK DN NAUPARE |  |  |  |  | Amount (euro)
1 | PUMPING STATION PS NAUPARE 1
2 | RESERVOIR R NAUPARE 1
3 | PUMPING STATION PS NAUPARE 2
4 | RESERVOIR R NAUPARE 2
5 | SOFTWARE SUPPORT
6 | AS-BUILT DOCUMENTATION PRODUCTION
7 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
I | DISTRIBUTION NETWORK DN NAUPARE | TOTAL carried to Summary C.
II | DISTRIBUTION NETWORK DN SOGOLJ-MESEVO
9 | PUMPING STATION PS SOGOLJ - MESEVO
9.1 | Supply, delivery and wiring of the PLC-4.11, type CJ1M or adequate |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
9.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
9.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
9.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
9.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
9.6 | The PLC-4.11 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. communication services to client data requests and command messages, coming from the authorised communication centre PLC-4.12,
e. diagnostic functions for measuring equipment and the PLC itself.
9.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
9.8 | Reconstruction of an existing motor control cabinet ROP, which means: |  | set | 1
o redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,
o installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,
o installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet.
9.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in pumping stations (PS).
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Flow meter transducer IC720
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2,S3,S4 Three-pole switch 20A/1-0-2/3P/V M10HEU3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC: PGR3131,2P,230VAC/12A
K8...K10 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K11 Single pole interface relay 24VDC, G2RV-SLC700 DC24
X1,2,3 Wire terminals 2.5 mm2
9.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
9.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
9.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors and an inlet pressure switch.
9.13 | Supply, delivery and installation of a pressure switch |  | pcs | 1
Adjustable pressure switch (pressostat), used for dry running protection, mounted on the suction pipe
Adjustable pressure range : 0.5-8 bar
Min differential pressure: 0.5 bar
Fitting: 0.5 inch
9.14 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
9.15 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
9.16 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND100 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
9.17 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the outlet of PS Šogolj-Meševo
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 100
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
9.18 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
9.19 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
9.20 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00-Y 3x2.5 10 Power supply 220VAC, 50Hz
W02 IyStY 8x2x0.6 10 ROMTK to ROP
W03 IyStY 1x2x0.6 20 To flooding detector probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 2x0.75 15 To inlet pressure sensor
W06 LiYCy 2x0.75 15 To outlet pressure sensor
W07 LiYCy 3x0.75 20 To outlet flow meter sensor
W08 LiYCy 2x0.75 20 To outlet flow meter sensor
W100 LiYCy 8x0.6 2 Comm, PLC-T96SR, RS232
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
9.21 | Construction works |  | set | 1
Construct a metal platform annex inside the PS, lengthen to the right from doorway, along the front wall to the right side wall, 1m wide and properly supported, in order to provide accommodation and access to the distribution cabinets ROMTK and ROP (if moved).
9 | PUMPING STATION PS SOGOLJ - MESEVO - TOTAL | Sub-total carried to Summary II
10 | RESERVOIR R MESEVO 1
10.1 | Supply, delivery and wiring of the PLC-4.12, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU12 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
CJ1W-ETN21 pcs 1
10.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
10.3 | Supply and delivery of an aerial |  | set | 1
Omnidirectional antenna:
Frequency range: 390-520MHz
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
10.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
10.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
10.6 | The PLC-4.12 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. diagnostic functions for measuring equipment and the PLC itself,
c. a set of communication functions:
o regular polling of all the communication slaves in a radio-modem network every 30s,
o buffering the most recently obtained data from the slaves, together with IO signals obtained directly through its own IO modules,
o sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL,
o sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request,
o reception of commans from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network, with higher priority than regular polls,
o sending an extra poll to the slave previously targeted by a command, to provide prompt command execution status,
o sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL.
10.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
10.8 | Reconstruction of the main distribution cabinet RO, |  | set | 1
which means installation of:
o F1, F2 two circuit breakers PGR4470, SI C10/2, intended for power supply of the separate CCMS cabinet ROMTK,
o DIN Rail Mounting Terminal Blocks-Clamps, 600V/25A rated, for stranded wire up to 2.5mm2 or solid wire up to 4mm2,
o various accessories: cable lugs, cable end sleeves, stranded isolated wire 1.5mm2 and 2.5mm2, heat shrink tubing, cable tags, device identification marks etc.
Reconstruction includes delivery, connecting and labelling of a cable PP00 3x2.5mm2 for the ROMTK power supply from the distribution cabinet RO.
10.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 PLC CJ1M-CPU12, 2xDI211, 1x0C201, 1XAD041-v1, 1xETN21
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
10.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
10.11 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Terminal unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width: 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used: IP V4, UDP, TCP, IC MP, Telnet, HTTP, FTP, SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Wind resistance 190 km/hr
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 1
Radio-device power supply, 90-220VAC/24VDC, min 0,3 A, indoor construction, with Ethernet by-pass pcs 1
Ethernet Surge Suppressor , for outdoor installation pcs 1
FTP cable cat.5e, patch, 30m pcs 1
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Radio-device and control module outdoor installation pcs 1
Set-up and configuration of radio-device and control module pcs 1
unspecified consumables pcs 1
Travel and accommodation expenses pcs 1
System commissioning pcs 1
Unspecified material pcs 1
10.12 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
10.13 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
10.14 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
10.15 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
10.16 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
10.17 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W03 IyStY 4x2x0.6 20 To storage level probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 5x0.75 20 To storage level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
10.18 | Construction works |  | set | 1
Construct an additional room leant on the front wall of the existing object, to the left of storage doorway, with a separate entrance, in order to provide accommodation for distribution cabinets.
10.19 | Electric power service obtaining |  | set | 1
Works and procedures necessary for electric power service providing: service request submission for 10.5kW, obtaining required approvals and permits, cable 4x35mm2 routing from the distribution network approx. 500m away, reinforced concrete utility poles installation, gas discharge surge protectors and power meter installation. Also includes all other works and taxes required by authorised power distribution company in order to obtain electric power service.
10 | RESERVOIR R MESEVO 1 - TOTAL | Sub-total carried to Summary II
11 | RESERVOIR R MESEVO 2
11.1 | Supply, delivery and wiring of the PLC-4.13, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
11.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
11.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
11.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
11.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
11.6 | The PLC-4.13 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests, coming from the authorised communication centre PLC-4.12,
c. diagnostic functions for measuring equipment and the PLC itself.
11.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
11.8 | Reconstruction of the main distribution cabinet RO, |  | set | 1
which means installation of:
o F1, F2 two circuit breakers PGR4470, SI C10/2, intended for power supply of the separate CCMS cabinet ROMTK,
o DIN Rail Mounting Terminal Blocks-Clamps, 600V/25A rated, for stranded wire up to 2.5mm2 or solid wire up to 4mm2,
o various accessories: cable lugs, cable end sleeves, stranded isolated wire 1.5mm2 and 2.5mm2, heat shrink tubing, cable tags, device identification marks etc.
Reconstruction includes delivery, connecting and labelling of a cable PP00 3x2.5mm2 for the ROMTK power supply from the distribution cabinet RO.
11.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
11.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
11.11 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
11.12 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
11.13 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
11.14 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
11.15 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
11.16 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W03 IyStY 4x2x0.6 20 To storage level probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 5x0.75 20 To storage level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
11.17 | Construction works |  | set | 1
Construct an additional room leant on the front wall of the existing object, to the left of storage doorway, with a separate entrance, in order to provide accommodation for distribution cabinets.
11.18 | Electric power service obtaining |  | set | 1
Works and procedures necessary for electric power service providing: service request submission for 10.5kW, obtaining required approvals and permits, cable 4x35mm2 routing from the distribution network approx. 50m away, reinforced concrete utility poles installation, gas discharge surge protectors and power meter installation. Also includes all other works and taxes required by authorised power distribution company in order to obtain electric power service.
11 | RESERVOIR R MESEVO 2 - TOTAL | Sub-total carried to Summary II
12 | HYDRO PRESS HP CEROVA
12.1 | Supply, delivery and wiring of the PLC-4.14, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
12.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
12.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
12.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
12.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
12.6 | The PLC-4.14 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. communication services to client data requests and command messages, coming from the authorised communication centre PLC-4.12,
e. diagnostic functions for measuring equipment and the PLC itself.
12.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
12.8 | Supply, delivery, installation and commissioning of a new motor control cabinet ROP, wall mounted in the object. |  | set | 1
The cabinet will contain:
o a main switch and an appropriate main circuit breaker,
o one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,
o three sets, each containing:
a. a DOL starter with auxiliary contacts for local and remote signalisation,
b. a three-pole circuit breaker with either auxiliary contacts or AC line monitor, status contacts intended for command logic and signalling.
c. appropriate bimetal thermostat protection with auxiliary contacts for command circuitry and signalling;
o command circuitry of the following characteristics
a. possibility of two duty pumps operation according to two outlet pressostats' signals, but only in local automatic mode,
b. possibility of duty-standby rotation changeover on every HP shutdown, but only in local automatic mode,
c. possibility of pump control from the ROMTK cabinet in remote operation modes, with no interference of duty rotation logic or outlet pressostat signals,
d. bimetal thermostat protection, circuit breaker protection and dry running protection must be incorporated regardless of operation mode.
o auxiliary contacts and relays for remote signalling of dry running protection status, outlet pressostats' signals, AC power supply status and motor statuses,
o local fault indicators,
o necessary wire terminals and clamps for interconnection with the equipment and the CCMS distribution cabinet;
12.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the hydro press object.
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in HP facilities.
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2 Three-pole switch 20A/1-0-2/3P/V M10HEU3
S3,S4 Three-pole switch 20A/1-0/3P/V M10HEA3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC, PGR3131,2P,230VAC/12A
K8 Single pole interface relay 220VAC, G2RV-SLC700 AC230
K9 Two pole interface relay 220VAC, PGR3131,2P,230VAC/12A
K10...13 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1,2,3,4 Wire terminals 2.5 mm2
12.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
12.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
12.12 | Supply, delivery and installation of limit pressure detector |  | pcs | 1
Electric contact manometer with two adjustable limit switches, used for alarming, type Teleoptik or equivalent
Measuring range : 0-16 bar
Fitting: 0.5 inch
12.13 | Supply, delivery and installation of a pressure switch |  | pcs | 1
Replacement of the existing defective pressostat used for dry running protection, mounted on the suction pipe, with a new adjustable pressure switch with the same purpose.
Adjustable pressure range : 0.5-8 bar
Min differential pressure: 0.5 bar
Fitting: 0.5 inch
12.14 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors and a limit pressure switch.
12.15 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
12.16 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
12.17 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
12.18 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
12.19 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz,
W02 IyStY 8x2x0.6 10 ROMTK to ROP, 220VAC
W04 IyStY 1x2x0.6 15 To flooding detector probes
W05 IyStY 1x2x0.6 40 Open door detector, 24VDC
W06 IyStY 1x2x0.6 15 Low outlet pressure detector
W07 IyStY 1x2x0.6 15 High outlet pressure detector
W08 LiYCy 2x0.75 15 To inlet pressure sensor
W09 LiYCy 3x0.75 15 To outlet pressure sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
12.20 | Construction works |  | set | 1
Construct a metal platform annex inside the HP, lengthen to the left from doorway, along the front wall to the left side wall, 1m wide and properly supported, in order to provide accommodation and access to the distribution cabinets ROMTK and ROP.
12 | HYDRO PRESS HP CEROVA - TOTAL | Sub-total carried to Summary II
13 | SOFTWARE SUPPORT
13.1 | The application software for the monitoring stations in CCC1 Lipovac and CCC2 Direkcija, which means configuration of additional a. variables - tags, b. mimic diagrams, c. reports, d. operator interfaces that concerns the distribution network DN Šogolj-Meševo. |  | set | 1
The application software for the main server in CCC1 Lipovac, which means configuration of communication and control capabilities concerning DN Šogolj-Meševo.
13.2 | The Master PLC-1.1 application software, which means additional communicational and control features necessary for integration of DN Šogolj-Meševo into the CCMS. |  | set | 1
13.3 | The application software for communication centre PLC-4.12, which means implementing of additional communication capabilities concerning locations within DN Šogolj-Meševo. |  | set | 1
13 | SOFTWARE SUPPORT - TOTAL | Sub-total carried to Summary II
14 | AS-BUILT DOCUMENTATION
14.1 | The production and assembly of as-built documentation KS DP09 |  | set | 1
for the distribution network DN Šogolj-Meševo.
14 | AS-BUILT DOCUMENTATION - TOTAL | Sub-total carried to Summary II
15 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
15.1 | Parameter adjustment and putting into operation the communication links between the authorised communication centre and all the objects within DN Šogolj-Meševo. Radio communication and data transfer testing. |  | set | 1
Parameter adjustment, testing and putting into operation measuring equipment, automation systems and remote controls.
Commissioning and performance verification
Putting into trial operation
The trial operation will last 15 days
15 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION - TOTAL | Sub-total carried to Summary II
II | SUMMARY II. - DISTRIBUTION NETWORK DN SOGOLJ-MESEVO |  |  |  |  | Amount (euro)
9 | PUMPING STATION PS SOGOLJ - MESEVO
10 | RESERVOIR R MESEVO 1
11 | RESERVOIR R MESEVO 2
12 | HYDRO PRESS HP CEROVA
13 | SOFTWARE SUPPORT
14 | AS-BUILT DOCUMENTATION PRODUCTION
15 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
II | DISTRIBUTION NETWORK DN SOGOLJ-MESEVO | TOTAL carried to Summary C.
C. | SUMMARY C - SUBSYSTEM “RASINA WALLY SYSTEM” |  |  |  |  | Amount (euro)
I | DISTRIBUTION NETWORK DN NAUPARE
II | DISTRIBUTION NETWORK DN SOGOLJ-MESEVO
C. | SUBSYSTEM “RASINA WALLY SYSTEM” | TOTAL carried to Bill No. 9
D. | SUBSYSTEM “MORAVA SYSTEM”
1 | PUMPING STATION PS SRNJE 1
1.1 | Supply, delivery and wiring of the PLC-5.17, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
1.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
1.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
1.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
1.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
1.6 | The PLC-5.17 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. communication services to client data requests and command messages, coming from the authorised communication centre PLC-5.23,
e. diagnostic functions for measuring equipment and the PLC itself.
1.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
1.8 | Reconstruction of an existing motor control cabinet ROP, which means: |  | set | 1
o installation of one new rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,
o upgrading of existing rotary switches with additional poles in order to provide selection signalisation into the CCMS,
o redesign of motor command circuitry, which means:
a. to reconnect wirings in order to provide both remote and local motor control,
b. to redefine the function of existing rotary switches in order to provide duty pump selection and appropriate signalisation into the CCMS,
c. to bypass upstream reservoir operating level signals when in remote operation mode,
o either replacement of plug fuses with circuit breakers or installation of additional AC line monitors after the fuses, in both cases with auxiliary contacts for command circuitry integration and signalisation into the CCMS,
o installation of auxiliary contacts, relays and clamps in order to provide all required monitoring signals to the CCMS distribution cabinet,
1.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in pumping stations (PS).
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Flow meter transducer IC720
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2,S3,S4 Three-pole switch 20A/1-0-2/3P/V M10HEU3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC: PGR3131,2P,230VAC/12A
K8...K10 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K11 Single pole interface relay 24VDC, G2RV-SLC700 DC24
X1,2,3 Wire terminals 2.5 mm2
1.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
1.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
1.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors.
1.13 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
1.14 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
1.15 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND100 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
1.16 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the outlet of PS Srnje 1
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 100
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
1.17 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
1.18 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
1.19 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00-Y 3x2.5 10 Power supply 220VAC, 50Hz
W02 IyStY 8x2x0.6 10 ROMTK to ROP
W03 IyStY 1x2x0.6 20 To flooding detector probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 2x0.75 15 To inlet pressure sensor
W06 LiYCy 2x0.75 15 To outlet pressure sensor
W07 LiYCy 3x0.75 20 To outlet flow meter sensor
W08 LiYCy 2x0.75 20 To outlet flow meter sensor
W100 LiYCy 8x0.6 2 Comm, PLC-T96SR, RS232
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
1.20 | Construction works |  | set | 1
Construct an additional room leant on the existing object, with a separate entrance, in order to provide accommodation for distribution cabinets ROMTK and ROP.
1 | PUMPING STATION PS SRNJE 1 - TOTAL | Sub-total carried to Summary D
2 | PUMPING STATION PS KRVAVICA-PADEZ AND RESERVOIR R SRNJE 1
2.1 | Supply, delivery and wiring of the PLC-5.18, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 3
CJ1W-OC201 pcs 1
CJ1W-AD081-V1 NL pcs 1
2.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
2.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
2.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
2.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
2.6 | The PLC-5.18 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre, for both pump groups,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. communication services to client data requests and command messages, coming from the authorised communication centre PLC-5.23,
e. diagnostic functions for measuring equipment and the PLC itself.
2.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
2.8 | Reconstruction of an existing motor control cabinet for the pumps supplying R Padež, which means: |  | set | 1
o redesign motor command circuitry:
a. eliminate the existing micro-PLC and reconnect wirings in order to provide both remote and local motor control,
b. redefine the function of existing rotary switches in order to provide duty pump selection and appropriate signalisation into the CCMS,
c. bypass upstream reservoir operating level signals when in remote operation mode,
o installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,
o installation of auxiliary contacts, relays and clamps in order to provide necessary monitoring signals to the CCMS cabinet.
Reconstruction of an existing motor control cabinet for the pumps supplying R Krvavica, which means:
o redesign motor command circuitry in order to provide both remote and local motor control,
o installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,
o installation of auxiliary contacts, relays and clamps in order to provide necessary monitoring signals to the CCMS cabinet.
2.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in a pumping station with adjacent storage reservoir (PSR).
The cabinet contains:
U1 PLC CJ1M-CPU11, 3xDI211, 1x0C201, 1XAD081-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Flow meter transducer IC720
U8 Flow meter transducer IC720
U9 Level transducer CS600
U10 Radio-modem T-96SR
U11 Over voltage protection FRD24 HF
U12 Over voltage protection FRD24 HF
U13 Over voltage protection FRD24 HF
U14 Over voltage protection VF230
U15 Aerial over voltage protection
U16 Level detector DN1
U17 Level detector DN2
U18 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2,S3,S4,S5 Three-pole switch 20A/1-0-2/3P/V M10HEU3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6,K7 Two pole interface relays 220VAC: PGR3131,2P,230VAC/12A
K8 Single pole interface relay 220VAC, G2RV-SLC700 AC230
K9 Two pole interface relay 220VAC: PGR3131,2P,230VAC/12A
K10,K11 Single pole interface relays 24VDC, G2RV-SLC700 DC24
K21...K25 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K26,K27 Two pole interface relays 220VAC: PGR3131,2P,230VAC/12A
K28 Single pole interface relay 220VAC, G2RV-SLC700 AC230
K29 Two pole interface relay 220VAC: PGR3131,2P,230VAC/12A
X1,2,3,4,5 Wire terminals 2.5 mm2
2.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
2.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
2.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors.
2.13 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
2.14 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
2.15 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND100 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
2.16 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the PS Krvavica-Padež outlet to R Padež
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 100
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
2.17 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND200 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
2.18 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the PS Krvavica-Padež outlet to R Krvavica
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 200
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
2.19 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
2.20 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
2.21 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
2.22 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
2.23 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
2.24 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 10 Power supply 220VAC, 50Hz
W02 IyStY 8x2x0.6 15 ROMTK to ROP Padež
W022 IyStY 8x2x0.6 15 ROMTK to ROP Krvavica
W03 IyStY 4x2x0.6 30 To reservoir level probes
W04 IyStY 1x2x0.6 20 To flooding detector probes
W05 IyStY 1x2x0.6 15 Open door detectors
W06 IyStY 1x2x0.6 30 Open door detectors
W07 LiYCy 2x0.75 15 Outlet pressure sensor Padež
W027 LiYCy 2x0.75 15 Outlet pressure sensor Krvavica
W08 LiYCy 3x0.75 20 Flow meter sensor, Padež
W09 LiYCy 2x0.75 20 Flow meter sensor, Padež
W028 LiYCy 3x0.75 20 Flow meter sensor, Krvavica
W029 LiYCy 2x0.75 20 Flow meter sensor, Krvavica
W10 LiYCy 5x0.75 30 To level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
2.25 | Construction works |  | set | 1
Construct a metal platform annex inside the PS, lengthen to the right from doorway, along the font wall to the right side wall, 1m wide and properly supported, in order to provide accommodation and access to the distribution cabinet ROMTK.
2 | PUMPING STATION PS KRVAVICA-PADEZ AND RESERVOIR R SRNJE 1 - TOTAL | Sub-total carried to Summary D
3 | RESERVOIR R KRVAVICA
3.1 | Supply, delivery and wiring of the PLC-5.21, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
3.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
3.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
3.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
3.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
3.6 | The PLC-5.21 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests, coming from the authorised communication centre PLC-5.23,
c. diagnostic functions for measuring equipment and the PLC itself.
3.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
3.8 | Reconstruction of the main distribution cabinet RO, |  | set | 1
which means installation of:
o F1, F2 two circuit breakers PGR4470, SI C10/2, intended for power supply of the separate CCMS cabinet ROMTK,
o DIN Rail Mounting Terminal Blocks-Clamps, 600V/25A rated, for stranded wire up to 2.5mm2 or solid wire up to 4mm2,
o various accessories: cable lugs, cable end sleeves, stranded isolated wire 1.5mm2 and 2.5mm2, heat shrink tubing, cable tags, device identification marks etc.
Reconstruction includes delivery, connecting and labelling of a cable PP00 3x2.5mm2 for the ROMTK power supply from the distribution cabinet RO.
3.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
3.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
3.11 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Central access unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used IP V4, UDP, TCP , IC MP, Telnet, HTTP , FTP , SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Software Upgrade remote downloaded in FLASH over RF link
Wind resistance 190 km/hr
Temperature range: -40°C to +55°C
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Terminal unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used IP V4, UDP, TCP , IC MP, Telnet, HTTP , FTP , SN MP
Network Management HTTP , TELN ET, FTP , SN MP Version 2c
Wind resistance 190 km/hr
Temperature range: -40°C to +55°C
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply 24VDC, power over Ethernet
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 2
radio-device power supply , 90-220VAC/24VDC, min 0,3 A, indoor, construction, with Ethernet by-pass
Ethernet Surge Suppressor , for outdoor installation pcs 2
FTP cable cat.5e, patch, 30m pcs 2
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Radio-device and control module outdoor installation pcs 2
Set-up and configuration of radio-device and control module pcs 2
Unspecified consumables pcs 1
3.12 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
3.13 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
3.14 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
3.15 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
3.16 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
3.17 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W03 IyStY 4x2x0.6 20 To storage level probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 5x0.75 20 To storage level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
3.18 | Electric power service obtaining |  | set | 1
Works and procedures necessary for electric power service providing: service request submission for 10.5kW, obtaining required approvals and permits, cable 4x35mm2 routing from the distribution network approx. 300m away, reinforced concrete utility poles installation, gas discharge surge protectors and power meter installation. Also includes all other works and taxes required by authorised power distribution company in order to obtain electric power service.
3 | RESERVOIR R KRVAVICA - TOTAL | Sub-total carried to Summary D
4 | RESERVOIR R PADEZ
4.1 | Supply, delivery and wiring of the PLC-5.22, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
4.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
4.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
4.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
4.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
4.6 | The PLC-5.22 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests, coming from the authorised communication centre PLC-5.23,
c. diagnostic functions for measuring equipment and the PLC itself.
4.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
4.8 | Reconstruction of the main distribution cabinet RO, |  | set | 1
which means installation of:
o F1, F2 two circuit breakers PGR4470, SI C10/2, intended for power supply of the separate CCMS cabinet ROMTK,
o DIN Rail Mounting Terminal Blocks-Clamps, 600V/25A rated, for stranded wire up to 2.5mm2 or solid wire up to 4mm2,
o various accessories: cable lugs, cable end sleeves, stranded isolated wire 1.5mm2 and 2.5mm2, heat shrink tubing, cable tags, device identification marks etc.
Reconstruction includes delivery, connecting and labelling of a cable PP00 3x2.5mm2 for the ROMTK power supply from the distribution cabinet RO.
4.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
4.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
4.11 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
4.12 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
4.13 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
4.14 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
4.15 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
4.16 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W03 IyStY 4x2x0.6 20 To storage level probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 5x0.75 20 To storage level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
4.17 | Electric power service obtaining |  | set | 1
Works and procedures necessary for electric power service providing: service request submission for 10.5kW, obtaining required approvals and permits, cable 4x35mm2 routing from the distribution network approx. 250m away, reinforced concrete utility poles installation, gas discharge surge protectors and power meter installation. Also includes all other works and taxes required by authorised power distribution company in order to obtain electric power service.
4 | RESERVOIR R PADEZ - TOTAL | Sub-total carried to Summary D
5 | PUMPING STATION PS GLOBARE
5.1 | Supply, delivery and wiring of the PLC-5.23, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU12 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
CJ1W-ETN21 pcs 1
5.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
5.3 | Supply and delivery of an aerial |  | set | 1
Omnidirectional antenna:
Frequency range: 390-520MHz
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
5.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
5.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
5.6 | The PLC-5.23 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. diagnostic functions for measuring equipment and the PLC itself,
e. a set of communication functions:
o regular polling of all the communication slaves in a radio-modem network every 30s,
o buffering the most recently obtained data from the slaves, together with IO signals obtained directly through its own IO modules,
o sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL,
o sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request,
o reception of commans from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network, with higher priority than regular polls,
o sending an extra poll to the slave previously targeted by a command, to provide prompt command execution status,
o sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL.
5.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
5.8 | Reconstruction of a designed motor control cabinet ROP, which means: |  | set | 1
o redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,
o installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,
o installation of auxiliary contacts, relays and wire terminals in order to provide necessary monitoring signals to the CCMS cabine
5.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in pumping stations (PS).
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1, 1xETN21
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Flow meter transducer IC720
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2,S3,S4 Three-pole switch 20A/1-0-2/3P/V M10HEU3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC: PGR3131,2P,230VAC/12A
K8...K10 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K11 Single pole interface relay 24VDC, G2RV-SLC700 DC24
X1,2,3 Wire terminals 2.5 mm2
5.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
5.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
5.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors.
5.13 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
5.14 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
5.15 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND50 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
5.16 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the outlet of PS Globare
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 50
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
5.17 | Supply, delivery, installation and commissioning of the wireless Ethernet equipment |  | set | 1
Terminal unit pcs 1
Frequency Range of Band U-NI 5470-5725 MHz
Channel Width 20 MHz
Channel Spacing 20 MHz channels in the allowable spectrum as assigned in 5 MHz increments.
Modulation Type High Index 2-level Frequency Shift Keying (FSK) optimised for interference rejection
Encryption DES, FIPS 197 certified AES
Carrier to Interference Ratio (C/I) <3
Antenna type: internal microstrip.
Antenna Beam Width: 3 dB antenna beam width 60deg., Azimuth and Elevation
Interface 10/100 Base T, half/full duplex. Rate auto negotiated (802.3 compliant)
Protocols Used: IP V4, UDP, TCP, IC MP, Telnet, HTTP, FTP, SN MP
Network Management: HTTP, TELNET, FTP, SN MP Version 2c
Wind resistance 190 km/hr
Radio-device, Ethernet communication interface and antenna, must be installed in original unique water-proof and UV resistant enclosure .
Device power supply: 24VDC, power over Ethernet
Passive antenna reflector : system gain, 3 dB, generated reflector 6deg, Azimuth and Elevation. To be delivered with clamps for radio unit and reflector pcs 1
Radio-device power supply, 90-220VAC/24VDC, min 0,3 A, indoor construction, with Ethernet by-pass pcs 1
Ethernet Surge Suppressor , for outdoor installation pcs 1
FTP cable cat.5e, patch, 30m pcs 1
Antenna mast, steel single-tube zinc-plated , diameter min. 75mm, two sections, total h=10m, with mounting clamp, earthing gland and shrouds. pcs 1
Radio-device and control module outdoor installation pcs 1
Set-up and configuration of radio-device and control module pcs 1
Unspecified consumables pcs 1
Travel and accommodation expenses pcs 1
System commissioning pcs 1
Unspecified material pcs 1
5.18 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
5.19 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
5.20 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00-Y 3x2.5 10 Power supply 220VAC, 50Hz
W02 IyStY 8x2x0.6 10 ROMTK to ROP
W03 IyStY 1x2x0.6 20 To flooding detector probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 2x0.75 15 To inlet pressure sensor
W06 LiYCy 2x0.75 15 To outlet pressure sensor
W07 LiYCy 3x0.75 20 To outlet flow meter sensor
W08 LiYCy 2x0.75 20 To outlet flow meter sensor
W100 LiYCy 8x0.6 2 Comm, PLC-T96SR, RS232
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
5 | PUMPING STATION PS GLOBARE - TOTAL | Sub-total carried to Summary D
6 | RESERVOIR R GLOBARE
6.1 | Supply, delivery and wiring of the PLC-5.24, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
6.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
6.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
6.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
6.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
6.6 | The PLC-5.24 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests, coming from the authorised communication centre PLC-5.23,
c. diagnostic functions for measuring equipment and the PLC itself.
6.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
6.8 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
6.9 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
6.10 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 1
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
6.11 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
6.12 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
6.13 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
6.14 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
6.15 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W03 IyStY 4x2x0.6 20 To storage level probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 5x0.75 20 To storage level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
6 | RESERVOIR R GLOBARE - TOTAL | Sub-total carried to Summary D
7 | PUMPING STATION PS SRNJE 2
7.1 | Supply, delivery and wiring of the PLC-5.19, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 2
CJ1W-OC201 pcs 1
CJ1W-AD041-V1 NL pcs 1
7.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
7.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
7.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
7.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
7.6 | The PLC-5.19 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,
c. continuous execution of protective procedures for the equipment and the water supply system,
d. communication services to client data requests and command messages, coming from the authorised communication centre PLC-5.23,
e. diagnostic functions for measuring equipment and the PLC itself.
7.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
7.8 | Reconstruction of an existing motor control cabinet ROP, which means: |  | set | 1
o installation of one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,
o installation of two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,
o redesign of motor command circuitry:
a. reconnect wirings in order to provide both remote and local motor control,
b. either replace the existing motor fuses with appropriate circuit breakers with auxiliary contacts, or install AC line monitors after the fuses for each motor, and integrate power status signal into the circuitry,
c. integrate rotary switches for duty pump selection and provide appropriate signalisation into the CCMS,
d. bypass upstream reservoir operating level signals when in remote operation mode;
o installation of auxiliary contacts, relays and clamps in order to provide necessary monitoring signals to the CCMS cabinet,
7.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in pumping stations (PS).
The cabinet contains:
U1 PLC CJ1M-CPU11, 2xDI211, 1x0C201, 1XAD041-v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Over voltage protection LPP4
U5 Digital display unit DP3v5
U6 Digital display unit DP3v5
U7 Flow meter transducer IC720
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN1
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
S2,S3,S4 Three-pole switch 20A/1-0-2/3P/V M10HEU3
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1...K5 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K6, K7 Two pole interface relays 220VAC: PGR3131,2P,230VAC/12A
K8...K10 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K11 Single pole interface relay 24VDC, G2RV-SLC700 DC24
X1,2,3 Wire terminals 2.5 mm2
7.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
7.11 | Supply of digital display, type DP3 or equivalent |  | pcs | 2
For presentation of inlet and outlet pressure measurement in ROMTK
Input 4-20mA, display range 0-100%, adjustable. LED display 13mm, 3+1/2 digits.
Supply 24VDC
Accuracy 0.2% +/-1 digit. Dimensions WxHxD 96x48x100, door mounted.
The digital display will be installed in the ROMTK, mounted on the door.
7.12 | Preparation of fittings for pressure sensor installation |  | set | 1
Mechanical works necessary for pressure sensor installation: pipe welding and conditioning, mounting of ball valve ½" with a bleed valve (petcock), pipe branch tee and fittings for installation of pressure sensors.
7.13 | Supply, delivery and installation of an absolute pressure transmitter |  | pcs | 2
Compact version
Characteristics:
• Available ranges (0... 16 ) bar.
• Two-wire (4-20)mA connection
• Electric output is either cable (standard length 2m) or connector.
• Zero suppression: 100% of range
• Elevation: usually 20% of range
additional corrections during transmitter operation in the range ±5%.
• Materials: electronic unit housing Al.Cu5.Mg1.55, diaphragm 316 Stainless
Steel, central section housing and process flange stainless steel.
• Process connection 1/2"R-M
• Mechanical protection IP65
Class 0.60
Linearity 0.4
Hysteresis 0.1
Repeatability 0.1
7.14 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
7.15 | Preparation of fittings for flow meter sensor installation |  | set | 1
Mechanical works necessary for flow sensor installation: o pipe conditioning, o supply, delivery and installation of two mounting flanges ND65 NP16, o supply and delivery of a pipe section having flanged ends, the same dimensions as a flow sensor.
7.16 | Delivery, installation and commissioning of an electromagnetic flow meter |  | set | 1
on the outlet of PS Srnje 2
Electromagnetic flow meter with display and current loop output, similar to type IC720 or equivalent with the following characteristics:
Nominal diameters DN 65
Hard rubber or polyurethane lining
High accuracy: ± 0.5% (option: ± 0.2%)
Robust field housing, IP 67 wall-mount housing for straightforward
Class 0.30
Linearity 0.1
Repeatability 0.1
Power supply: 24VDC ; power consumption: <5W
Display: 122x32 dots LCD graphical display with backlight
Configuring: numerical via keypad, range, measurement unit, sensitivity etc.
Output: galvanically insulated from the other circuits; Insulation: R>100Mohm, V>1500V
Output type: current loop, 4-20mA. two-wire connection, user configurable range
reverse polarity protection: yes
maximum output current: 24 mA
resolution: 14 bits (1 uA)
Switch outputs:
pulse for external totalizer, 0.1A, 250V photorelay
configurable: flow indicator or device status (OK/fault), 0.1A, 250V photorelay
Sensor input:
type: differential, AC coupled ; Impedance: 2 Mohm; resolution:16 bit
oversampling: x100 ; sensitivity:0.1 uV
Communication: MODBUS RTU, RS485, half duplex, 56Kbps, 8 bits, no parity, 1 stop bit
Ambient temperature: -20…+70 0C
Housing: 96x96x60 mm (WxHxD), for door mounting, distribution cabinet RO MTK
7.17 | Supply, delivery, installation and wiring of a conductive level detector machine room flooding detector, type DN1 or equivalent |  | pcs | 1
Two pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
7.18 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
7.19 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00-Y 3x2.5 10 Power supply 220VAC, 50Hz
W02 IyStY 8x2x0.6 10 ROMTK to ROP
W03 IyStY 1x2x0.6 20 To flooding detector probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 2x0.75 15 To inlet pressure sensor
W06 LiYCy 2x0.75 15 To outlet pressure sensor
W07 LiYCy 3x0.75 20 To outlet flow meter sensor
W08 LiYCy 2x0.75 20 To outlet flow meter sensor
W100 LiYCy 8x0.6 2 Comm, PLC-T96SR, RS232
W101 Antenna cable
The scope of works include plastic ducting, as well as cable end preparation and labelling.
7.20 | Construction works |  | set | 1
Construct an additional room leant on the existing object, with a separate entrance, in order to provide accommodation for distribution cabinets ROMTK and ROP.
7 | PUMPING STATION PS SRNJE 2 - TOTAL | Sub-total carried to Summary D
8 | RESERVOIR R SRNJE 2
8.1 | Supply, delivery and wiring of the PLC-5.20, type CJ1M |  | set | 1
Power supply unit: CJ1W-PD025 pcs 1
CPU - CJ1M-CPU11 pcs 1
CJ1W-ID211 NL pcs 1
CJ1W-AD041-V1 NL pcs 1
8.2 | Supply, delivery, installation and commissioning of the radio-communication equipment T96SR and an accompanying aerial system |  | set | 1
Radio-general Frequency Range: 380–512 MHz Channel Bandwidth:12.5 or 25 kHz 12.5 or 25 kHz 12.5 or 25 kHz IC Emission Designators:16K0F1D, 15K3F1D, 15K0F1D, 16K0F1D, 16K0F1D, 15K3F1D,11K0F1D, 9K30F1D 11K0F1D, 9K30F1D,11K0F1D, 9K30F1D European Approval :CE Mark (403–470 MHz) ETSI :300.113 (403–470 MHz) Current Drain Transmit: 13.3 VDC 1800 mA Receive @ 13.3 VDC 125 mA Operating Voltage : 10–16 VDC Operating Temperature : -30°C to +60°C Operating Mode: Simplex or half-duplex RF Connector: SMA Data I/O Connector : DE-15 female Front Panel Indicators : min. PWR, TX, RX Timeout Timer: 60 seconds switchable on/off Diagnostics Online: Supply Voltage, Internal Temp., Forward and Reverse Power, RSSI Diagnostics Offline: Above, plus: Tx B+ Voltage, Analog Supply Voltage, Tx Test Tones Transmitter Bandwidth without tuning :450–470: 20 MHz RF Output Power Adjustable:1–5 watts @ 13.6 V Duty Cycle: 50% @ 5 watts, 30 seconds maximum transmit Frequency Stability :1.5 ppm Spurious and Harmonic Emission: -38 dBm (-75 dBc) FM Hum and Noise: -45 dB @ 25 kHz ; -40 dB @ 12.5 kHz Tx Attack Time: < 7 msec Receiver Frequency Stability : 1.5 ppm Sensitivity: < 0.35 μV at 12 dB SINAD Selectivity: 75 dB @ 25 kHz; 65 dB @ 12.5 kHz Intermodulation:75 dB Spurious and Image Rejection: 75 dB FM Hum and Noise:-48 dB @ 25 kHz ; -40 dB @ 12.5 kHz Conducted Spurious : < -57 dBm Rx Attack Time: < 7 ms Modem Data Rate: 4800, 9600, or 19200(user selectable) Signal Level:EIA RS-232C Data Format: Asynchronous, Serial, Transparent Word Length: 7 or 8 bit words, 1 or 2 stop bits Parity: Even, Odd, or None2 Handshake:RTS–CTS RTS/CTS : Delay 30 msec Modulation:DRCMSK Bit Error Rate:Better than 1 x 10-5 @ 1.0 μV at 9600 half channel. Better than 1 x 10-6 @ 1.0 μV at 9600 and 4800 full channel. Better than 2 x 10-5 @ 1.7 μV at 19200 full channel.
8.3 | Supply and delivery of an aerial |  | set | 1
Directional antenna:
Frequency range: 390-520MHz
Type: corner yagi, gain: 11 dBi
Connector: N-female, connectors N-male -2 pcs.
Coaxial cable: 20m:
Construction: lead-solid copper / shield-braided
Nom.diamter: 0.400 inch; Attenuation@450MHz: 9.19 dB/100m
Cable grounding kit: 2 pcs; Cable hangers: 20 pcs; Full metal construction
Single cable hanger, with metal clip, Round mast adaptor, Sealing material
8.4 | Installation of the aerial system |  | set | 1
Coaxial cable RG-213/U installation, crimping and earthing, including:
o Antenna N-connectors pcs 2
o RG213 – coaxial cable 15 m
o Cable earthing UEK1 pcs 1
o Patch cable N-N 1 m
8.5 | Supply, delivery and installation of an aerial mast |  | set | 1
Aerial mast: zinc coated 2" steel pole, 6m high, bracketed to the wall or on the roof of the object, where appropriate
Mounting of aerial system, installation of 15m RG213/U cable, crimping and connecting.
Connecting of the aerial mast to lightning protection and earthing installation, by means of zinc coated metal strip, according to existing legislation.
8.6 | The PLC-5.20 application software |  | set | 1
The software should provide:
a. immediate acquisition of all signals connected to PLC's I/O modules,
b. communication services to client data requests, coming from the authorised communication centre PLC-5.23,
c. diagnostic functions for measuring equipment and the PLC itself.
8.7 | Supply, delivery and installation of over-voltage protectors |  | pcs | 4
Over voltage protectors for analogue signals, type TT-2-PE-24VDC or equivalent.
8.8 | Reconstruction of the main distribution cabinet RO, |  | set | 1
which means installation of:
o F1, F2 two circuit breakers PGR4470, SI C10/2, intended for power supply of the separate CCMS cabinet ROMTK,
o DIN Rail Mounting Terminal Blocks-Clamps, 600V/25A rated, for stranded wire up to 2.5mm2 or solid wire up to 4mm2,
o various accessories: cable lugs, cable end sleeves, stranded isolated wire 1.5mm2 and 2.5mm2, heat shrink tubing, cable tags, device identification marks etc.
Reconstruction includes delivery, connecting and labelling of a cable PP00 3x2.5mm2 for the ROMTK power supply from the distribution cabinet RO.
8.9 | Supply, delivery, installation and connecting of ROMTK distribution cabinet, |  | set | 1
wall mounted in the object
The distribution cabinet should be made of cold-rolled sheet-steel, thickness 1.5mm, polyester structural powder-coated, providing protection degree IP55, with a single door, overall dimensions WxHxD 600x800x250 mm. Cable entry is from the bottom of the cabinet. The cabinet is delivered completely connected and tested. Specification is made according to the typical connection diagram for the ROMTK in storage reservoirs (R).
The cabinet contains:
U1 Programmable logic controller PLC CJ1M-CPU11, 1xDI211, 1XAD041- v1
U2 UPS SLAC24,
U3 Sealed lead acid batteries 2 x 12VDC/18Ah
U4 Level transducer CS600
U8 Radio-modem T-96SR
U9 Over voltage protection FRD24 HF
U10 Over voltage protection FRD24 HF
U11 Over voltage protection FRD24 HF
U12 Over voltage protection VF230
U13 Aerial over voltage protection
U14 Level detector DN2
U15 Level detector DN3
S1 Two-pole switch 20A/0-1/1P/V M10HEA1
F0 Circuit breaker PGR4470 SI C10/2
F1-2 Circuit breaker PGR4470 SI C6/1
F10 Circuit breaker PGR4470 SI C6/2
F11 Circuit breaker PGR4470 SI C2/1
t Thermostat
GR Anti-condensation heater
P1 Single phase socket
MP Open door detector
H0 Interior cabinet lighting 220VAC
K1 Single pole interface relays 220VAC, G2RV-SLC700 AC230
K2 Single pole interface relays 24VDC, G2RV-SLC700 DC24
X1...X4 Wire terminals 2.5mm2
8.10 | Supply, delivery and installation of the UPS for the ROMTK |  | set | 1
The UPS inside ROMTK must have the following characteristics:
Input voltage preregulation, "soft start" on power up, switching converter circuit,
status outputs and indicator system.
Supply voltage: 180. .240 V, 50 Hz; Power: max. 250W
Battery: 24V nominal, lead battery ; Capacity: min. 18 Ah
Electricity charge: max.1.5A (3A optional); Charging voltage: 27.9 V max
Thermal protection: yes
24V output (mains 220V):
Voltage: 23.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Output 24V (battery power):
Voltage: Battery voltage - 0.25V
Current: limited to 5A
Thermal protection: no
12V output:
Voltage: 13.2V + / - 2%
Current: limited to 3A
Thermal protection: yes
Status Output:
POWER OK: Threshold 23V - signals the presence of mains power
ACCU OK: Threshod 22.2V/22V - signals that battery is not empty
BACKUP: Threshold 20V - The device moved the power from batteries
CHARGING: Threshold 0.8A - Charging current greater than 0.8A
Display system - alphanumeric display to display measured values:
"Iout [A]” ,output current , output 24V
"Vout [V]”, output voltage, output 24V
"Vacc: [V]”, battery voltage
"Ichg: [A]", charging current
"Vaux: [V]” voltage control circuits pcs 1
VRLA maintenance free 'sealed' lead-acid battery UL12-18, 12V 18Ah pcs 2
All mounted in the ROMTK cabinet Complete
8.11 | Supply. delivery and installation of residual chlorine analyser, type Depolox or equivalent |  | set | 1
The analyser contains:
A) Depolox basic module
analogue current output 4-20 mA
B) Depolox wall mounted sensor
conductivity > 300mS
C) Accessories:
mounting accessories
D) Sampling pump
Testing and putting into operation.
8.12 | Delivery, installation and connecting of hydrostatic level transmitter |  | pcs | 2
Hydrostatic Level and Pressure Transmitter with display and current loop output, similar to type CS600 or equivalent, with the following characteristics Sensor: piezoresistive bridge Sensor material: Si, diaphragm AISI 316 SS Stainless Steel, probe housing stainless steel 4574. • Probe diameter 30 mm • Probe cable length 11m Ambient temperature: -20…+70 0C Housing: 96x48x60 mm (WxHxD) Display unit: Display: 4 digits 7 segm.LCD with sign, 15.2 mm digit height Configuring: numerical via keypad, range, measurement unit, additional offset, fluid density and time constant can be set Output type: current loop, 4-20mA. two-wire connection, user configurable range reverse polarity protection: yes maximum output current: 24 mA resolution: 14 bits (1 uA) Supply voltage: 10V..42VDC Electric output is connector, wire diameter 0.3..2.5 mm2 Input: Zero suppression: 100% of range Span: 10%...120% of range sensor fault detection: sensor excitation, sensor output thermal compensation: digital (numerical) Offset: <3mm Resolution: 1mm (10m range) Class 0.20 Linearity 0.1 Hysteresis 0.05 Repeatability 0.05 Standard range: 10 m H2O
8.13 | Supply and installation of open door detector |  | pcs | 2
Open door switch with lever
Type E400-00-PM or equivalent
8.14 | Supply, delivery, installation and wiring of a conductive level detector operating level detector intended for pump control, type DN2 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
8.15 | Supply, delivery, installation and wiring of a conductive level detector minimum and maximum level detector, type DN3 or equivalent |  | pcs | 1
Three pendular electrodes made of stainless steel 4574, 10m long, with a junction box
Seam sealer: Epoxide, standard MIL 1-16-923
Cable capacitance < 0.22uF, max cable length 2.2km
Low AC voltage probe excitation
8.16 | Supply, delivery and installation of the mounting brackets |  | pcs | 1
Wall brackets intended for mounting level detector probes and a level sensor.
Produced of L-profile steel bar, rust protected and painted, with cable glands.
8.17 | Cable delivery, installation and connecting |  | set | 1
Cable list
Label Type Cross-section (mm2) Length (m) Remark
W00 PP00 3x2.5 20 Power supply 220VAC, 50Hz
W03 IyStY 4x2x0.6 20 To storage level probes
W04 IyStY 1x2x0.6 20 Open door detector
W05 LiYCy 5x0.75 20 To storage level sensor
W100 LiYCy 3x0.75 2 Comm. cable, PLC-T96SR
W101 Antenna cable
8.18 | Electric power service obtaining |  | set | 1
Works and procedures necessary for electric power service providing: service request submission for 10.5kW, obtaining required approvals and permits, cable 4x35mm2 routing from the distribution network approx. 300m away, reinforced concrete utility poles installation, gas discharge surge protectors and power meter installation. Also includes all other works and taxes required by authorised power distribution company in order to obtain electric power service.
8 | RESERVOIR R SRNJE 2 - TOTAL | Sub-total carried to Summary D
9 | SOFTWARE SUPPORT
9.1 | The application software for the monitoring stations in CCC1 Lipovac and CCC2 Direkcija, which means configuration of additional a. variables - tags, b. mimic diagrams, c. reports, d. operator interfaces that concerns the distribution network DN Srnje. |  | set | 1
The application software for the main server in CCC1 Lipovac, which means configuration of communication and control capabilities concerning DN Srnje.
9.2 | The Master PLC-1.1 application software, which means additional communicational and control features necessary for integration of DN Srnje into the CCMS. |  | set | 1
9.3 | The application software for communication centre PLC-5.23, which means implementing of additional communication capabilities concerning locations within DN Srnje. |  | set | 1
9 | SOFTWARE SUPPORT - TOTAL | Sub-total carried to Summary D
10 | AS-BUILT DOCUMENTATION
10.1 | The production and assembly of as-built documentation KS DP09 |  | set | 1
for the distribution network DN Srnje.
10 | AS-BUILT DOCUMENTATION - TOTAL | Sub-total carried to Summary D
11 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
11.1 | Parameter adjustment and putting into operation the communication links between the authorised communication centre and all the objects within DN Srnje. Radio communication and data transfer testing. |  | set | 1
Parameter adjustment, testing and putting into operation measuring equipment, automation systems and remote controls.
Commissioning and performance verification
Putting into trial operation
The trial operation will last 15 days
11 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION - TOTAL | Sub-total carried to Summary D
D | SUMMARY D - SUBSYSTEM “MORAVA SYSTEM” |  |  |  |  | Amount (euro)
1 | PUMPING STATION PS SRNJE 1
2 | PUMPING STATION PS KRVAVICA-PADEZ AND RESERVOIR R SRNJE 1
3 | RESERVOIR R KRVAVICA
4 | RESERVOIR R PADEZ
5 | PUMPING STATION PS GLOBARE
6 | RESERVOIR R GLOBARE
7 | PUMPING STATION PS SRNJE 2
8 | RESERVOIR R SRNJE 2
9 | SOFTWARE SUPPORT
10 | AS-BUILT DOCUMENTATION
11 | ADJUSTMENT, TESTING AND PUTTING INTO OPERATION
D. | SUBSYSTEM “MORAVA SYSTEM” | TOTAL carried to Bill No.9
| SUMMARY BILL No.2 - CENTRALISED CONTROL AND MONITORING SYSTEM FOR THE REGIONAL WATER SUPPLY SYSTEM CELIJE |  |  |  |  | Amount (euro)
A | SUMMARY A
B | SUMMARY B
C | SUMMARY C
D | SUMMARY D
Bill No.9 | CENTRALISED CONTROL AND MONITORING SYSTEM FOR THE REGIONAL WATER SUPPLY SYSTEM CELIJE | TOTAL carried to Grand Summary - PART 2

## Bill No.10 - MCB
Bill No. 11 - MCB CICEVAC, VARVARIN, STALAC
Item | Description | Close specification | Unit | Qty. | Rate (Euro) | Amount (Euro)
A | CIVIL WORKS
I | PRELIMINARY WORKS
1.1 | Preliminary survey works, establishing centrelines reference points and grades |  | sum | 3
1.2 | Clearing, grubbing and removal of trees, cutting and removal of asphalt and pavement, kerbs, sidewalks and other surfaces or obstructions on project locations |  | m2 | 220
I | PRELIMINARY WORKS - TOTAL | Sub-total carried to Summary A.
II | EARTHWORKS
2.1 | Excavation in pipe trench and for vault foundations including all necessary grading, sheeting, shoring and dewatering.
2.1.1 | Excavation for vault foundations |  | m3 | 450
2.1.2 | Excavation for pipe trenches |  | m3 | 35
2.2 | Purchase, transportation and installation of sand and gravel
2.2.1 | Sand for pipe bedding, d=10cm |  | m3 | 6
2.2.2 | Sandy-gravel material Dmax=20mm, as pipe surround |  | m3 | 11
2.2.3 | Compacted gravel under base slab |  | m3 | 9.1
2.3 | Backfilling of pipe trench and around valve vault walls with selected excavated material including mechanical compaction in layers not exceeding 200 mm. |  | m3 | 270
2.4 | Disposal of surplus excavated material to designated spoil |  | m3 | 141
II | EARTHWORKS - TOTAL | Sub-total carried to Summary A.
III | CONCRETE WORKS
3.1 | Blinding concrete base under valve vaults base slab, grade C15, 50 mm thick |  | m2 | 101
3.2 | Reinforced water-tight (class V6) concrete to valve vaults, grade C30
3.2.1 | base slab |  | m3 | 21.9
3.2.2 | walls |  | m3 | 31.4
3.2.3 | top slab |  | m3 | 11.1
III. | CONCRETE WORKS - TOTAL | Sub-total carried to Summary A.
IV | REINFORCEMENT WORKS
4.1 | Purchase, transportation, bending and installation of ribbed reinforcement in valve vaults, RA400/500. |  | kg | 5474
IV | REINFORCEMENT WORKS - TOTAL: | Sub-total carried to Summary A.
V | IRONMONGERY WORKS
Note: Cost of works include complete anti-corrosion protection, all joining and auxiliary material.
5.1 | Access ladder with back protection; H=2,5 m |  | pcs | 6
5.2 | Chequer plate access cover with frame and padlock
5.2.1 | 80 x 100 cm |  | pcs | 6
5.2.2 | Dia. 70cm |  | pcs | 6
5.3 | Steel ventilation pipes Ø108/4mm as per details shown in drawings.
5.3.1 | L=1,0 m |  | pcs | 3
5.3.2 | H=3,0 m |  | pcs | 3
5.4 | Metal ladder over pipe for access and maintenance |  | pcs | 6
V | IRONMONGERY WORKS - TOTAL: | Sub-total carried to Summary A.
VI | MISCELLANEOUS WORKS
6.1 | Preparation of as built drawings and update of cadastral maps. |  | sum | 1
6.2 | Hydraulic tests of water-tightness of pipes |  | sum | 1
6.3 | Flushing and disinfection of pipeworks |  | sum | 1
VI | MISCELLANEOUS WORKS - TOTAL: | Sub-total carried to Summary A.
A. | SUMMARY A - CIVIL WORKS |  |  |  |  | Amount (euro)
I | PRELIMINARY WORKS
II | EARTHWORKS
III | CONCRETE WORKS
IV | REINFORCEMENT WORKS
V | IRONMONGERY WORKS
VI | MISCELLANEOUS WORKS
A. | MCB CICEVAC, VARVARIN, STALAC - CIVIL WORKS | TOTAL carried to Summary Bill No. 10
B. | HYDRO - MECHANICAL EQUIPMENT
I | PRESSURE AND FLOW CONTROL SYSTEM CICEVAC
Supply, install and check online:
1.1 | Needle valve DN250/PN10, electrically driven | 1.1 & 2.1. | pcs | 2
1.2 | Gate valve DN250/PN10, manually operated | 1.1 & 2.2. | pcs | 4
1.3 | Dismantling joint DN250/PN10 | 1.1 & 2.3. | pcs | 6
1.4 | Strainer, DN250/PN10 | 1.1 & 2.4. | pcs | 2
1.5 | Manometer (0-10bar) with push button piston (or three way tap) | 1.1 & 2.5 | pcs | 4
1.6 | Submersible drainage pump with hose Q=141 l/min, H=5m, P=0.5kW | 1.1 & 2.6 | set | 1
1.7 | Pipes,flanges, fittings and supports | 1.1 & 2.7.& 2.8.; Drawings: M0-1 and M0-2 | kg | 1150
I | PRESSURE AND FLOW CONTROL SYSTEM CICEVAC - TOTAL | Sub-total carried to Summary B.
II | PRESSURE AND FLOW CONTROL SYSTEM VARVARIN
Supply, install and check online:
2.1 | Needle valve DN250/PN10, electrically driven | 1.2 & 2.1. | pcs | 2
2.2 | Gate valve DN250/PN10, manually operated | 1.2 & 2.2. | pcs | 4
2.3 | Dismantling joint DN250/PN10 | 1.2 & 2.3. | pcs | 6
2.4 | Strainer, DN250/PN10 | 1.2 & 2.4. | pcs | 2
2.5 | Manometer (0-10bar) with push button piston (or three way tap) | 1.2 & 2.5 | pcs | 4
2.6 | Submersible drainage pump with hose Q=141 l/min, H=5m, P=0.5kW | 1.2 & 2.6 | set | 1
2.7 | Pipes,flanges, fittings and supports | 1.2 & 2.7.& 2.8.; Drawings: M0-3 and M0-4 | kg | 1150
II | PRESSURE AND FLOW CONTROL SYSTEM VARVARIN - TOTAL | Sub-total carried to Summary B.
III | PRESSURE AND FLOW CONTROL SYSTEM STALAC
Supply, install and check online:
3.1 | Needle valve DN150/PN10, electrically driven | 1.3 & 2.1. | pcs | 2
3.2 | Gate valve DN150/PN10, manually operated | 1.3 & 2.2. | pcs | 4
3.3 | Dismantling joint DN150/PN10 | 1.3 & 2.3. | pcs | 6
3.4 | Strainer, DN150/PN10 | 1.3 & 2.4. | pcs | 2
3.5 | Manometer (0-10bar) with push button piston (or three way tap) | 1.3 & 2.5 | pcs | 4
3.6 | Submersible drainage pump with hose Q=141 l/min, H=5m, P=0.5kW | 1.3 & 2.6 | compl. | 1
3.7 | Pipes,flanges, fittings and supports | 1.3 & 2.7.& 2.8.; Drawings: M0-5 and M0-6 | kg | 490
III. | PRESSURE AND FLOW CONTROL SYSTEM STALAC - TOTAL | Sub-total carried to Summary B.
B. | SUMMARY B. - MCB CICEVAC, VARVARIN, STALAC – MECHANICAL EQUIPMENT |  |  |  |  | Amount (euro)
I | PRESSURE AND FLOW CONTROL SYSTEM CICEVAC
II | PRESSURE AND FLOW CONTROL SYSTEM VARVARIN
III | PRESSURE AND FLOW CONTROL SYSTEM STALAC
B. | MCB CICEVAC, VARVARIN, STALAC – MECHANICAL EQUIPMENT | TOTAL carried to Summary Bill No. 10
| SUMMARY BILL No. 10 - MCB CICEVAC, VARVARIN, STALAC |  |  |  |  | Amount (euro)
A | CIVIL WORKS
B. | HYDRO - MECHANICAL EQUIPMENT
BILL No.10 | MCB CICEVAC, VARVARIN, STALAC | TOTAL carried to Grand Summary - PART 2

## Bill No.11 MCB I - WT Varvarin
Bill No.11 - PIPELINE: MCB I - WATER TANK VARVARIN
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
A | PIPELINE
I | PRELIMINARY WORK
I.1. | Ground clearning along pipeline from bushes and object. | B.2. | 4630.08 | m2
I | PRELIMINARY WORK -TOTAL | Sub-total carried to Summary A.
II | EARTH WORK | B.2.
II.1. | Excavation
II.1.1. | Excaution in ground of III class. According to tehnical conditions and ditailes from project . Widht of excavation is 90cm. | B.2.
II.1.2. | Machine excavation of the trench, L=3.086,72 m | B.2.6. | 4722.6816 | m3
II.1.3. | Additional machine excavation for the object on the ppeline route | B.2.6.
II.1.3.1. | Manhole for air valve | B.2.6. | 150 | m3
II.1.3.2. | Manhole for air valve | B.2.6. | 60 | m3
II.1.3.3. | Handy work excavation on places of montage extensions | B.2.3. | 150 | m3
II | EARTH WORK - TOTAL | Sub-total carried to Summary A.
III | FILLING
III.1. | Supply,transport, spreding, tamping of sand for a screeded bed according to tehnical conditions and plans. | B.2.4.
III.1.1. | Send in the trench under pipes Ø 400mm | B.2.4. | 555 | m3
III.2. | Trench covering with selected material from the excavation and object on the route. | B.3.1.1. | 3882.68 | m3
III.3. | Supply,transport and installation of gravel under roads. | B.2. | 450 | m3
III.4. | Making stratum from sinking gravel undred manholes according to tehnical conditions and plans. | B.2.
III.4.1. | Manhole for air valve 4 pcs | B.2. | 2 | m3
III.4.2. | Manhole for outlet valve 3 pcs | B.2. | 1.2 | m3
III.5. | Taking out of surplus excavation material on the waste for more 1,00km. In the price, the loading, the outloading and scattering of materials is accounted. | B.2. | 840 | m3
III | FILLING - TOTAL | Sub-total carried to Summary A.
IV | CONCRETE WORKS | B.6.
IV.1. | Nonreinforced concrete-under manholes plates | B.6. | 15 | m3
IV.2. | Reinforced concrete | B.6.
IV.2.1. | Making manholes on the pipeline route of watertightness concrete MB30. | B.6.
IV.2.1.1. | Manhole for air valve 4 pcs | B.6. | 37 | m3
IV.2.1.2. | Manhole for air valve 3 pcs | B.6. | 16 | m3
IV | CONCRETE WORKS - TOTAL | Sub-total carried to Summary A.
V | REINFORCEMENT | B.8.
V.1. | Reinforcing steel RA 400/500 for manhole object on pipeline route according tehnical condations and plans. | B.8. | 5900 | kg
V | REINFORCEMENT - TOTAL | Sub-total carried to Summary A.
VI | ASSEMBLY WORK | B.3.
VI.1. | Polythene pipes Ø 400 PE 100 working pressure 10 bar b=23.7 | B.3.1. | 3200 | m
VI.2. | Steel pipes Ø508 =6,3mm - sinking under roads. | B.3. | 12 | m
VI.3. | Steel pipes Ø350 -making T pieces | B.3. | 10 | m
VI.4. | Polythene arch Ø400/60° | B.3.3. | 1 | kom
VI.5. | Polythene archØ400/45° | B.3.3. | 1 | kom
VI.6. | Polythene arch Ø400/37° | B.3.3. | 1 | kom
VI.7. | Polythene arch Ø400/30° | B.3.3. | 1 | kom
VI.8. | Polythene arch Ø400/27° | B.3.3. | 1 | kom
VI | ASSEMBLY WORK - TOTAL | Sub-total carried to Summary A.
VII | PRESSURE TESTING | B.5.1.
VII.1 | Pressure testing polythene pipes Ø 400 b=23,7 PE 100, working pressure10 bar | B.5.1. | 3498.72 | m
VII | PRESSURE TESTING - TOTAL | Sub-total carried to Summary A.
VIII | WASHING OUT AND DESINFECTION | B.5.3.
VIII.1 | Washing out and desinfection polythene pipes Ø 400 both with reinforcing and phases pices | B.5.3. | 5356.72 | m
VIII | WASHING OUT AND DESINFECTION - TOTAL | Sub-total carried to Summary A.
IX | CROSSING WITH MAJOR ROAD
IX.1 | Crossing with highway Kruševac-Varvarin ,sinking protective steel pipe Ø508 b =6,3, L=12m. | A.1.1. | 12 | m
IX | CROSSING WITH MAJOR ROAD - TOTAL | Sub-total carried to Summary A.
X | FITTINGS
X.1. | Manhole for air valve
X.1.1 | Quill 400 NP 10 | A.1.4.. | 8 | pcs
X.1.2 | Steel reductor 400/500 | A.1.4.. | 8 | pcs
X.1.3 | T piece 350/80 swith welded flange NP10. | A.1.4.. | 4 | pcs
X.1.4 | Euro coverØ80/10 | A.1.5.1. | 4 | pcs
X.1.5 | Euro cover Ø350/10 | A.1.5.1. | 1 | pcs
X.1.6 | MDDA Ø350/10 | A.1.4.. | 1 | pcs
X.1.7 | Air valve Ø80/10 | A.1.5.2. | 4 | pcs
X.2. | Manhole for discharge
X.2.1 | T pices 350/80 NP10 with the flange | A.1.4.. | 6 | pcs
X.2.2 | Quill with reductor 400/300 NP10 bara. | A.1.4.. | 6 | pcs
X.2.3 | T pices 80/80 NP10 bar with the flange. | A.1.4.. | 3 | pcs
X.2.4 | Euro cover Ø80/10 | A.1.5.1. | 6 | pcs
X.2.5 | Euro cover Ø350/10 | A.1.5.1. | 3 | pcs
X.2.6 | Q piece Ø80/90° NP10 | A.1.5.1. | 3 | pcs
X.2.7 | N piece Ø80° NP10 | A.1.5.1. | 9 | pcs
X.2.8 | Hidrant Ø80° NP10 | A.1.5.3 | 3 | pcs
X.2.9 | MDDA Ø350/10 | A.1.4.. | 3 | pcs
X | FITTINGS - TOTAL | Sub-total carried to Summary A.
XI | LOCKSMITH'S WORK
XI.1 | Cover of grey cast carrying 50kN for the manhole for discharge and for the manhole for valve . 60 x 60cm |  | 7 | pcs
XI.2 | Creeper E shaped for subsidence in the manhole, is placed in concrete wall. Account by price. For air valve. |  | 70 | pcs
XI.3 | Ventilation pipe with ventilation cap according to details from the project. |  | 4 | pcs
XI | LOCKSMITH'S WORK - TOTAL | Sub-total carried to Summary A.
XII | WATERPROOFING
XII.1 | Waterproofing for manholes object on the pipeline rout. Account by m2 for all manholes - from the inner side |  | 280 | m2
XII | WATERPROOFING - TOTAL | Sub-total carried to Summary A.
XIII | MARKING
XIII.1. | Marking the pipeline by concrete stanchions with engaged brass boards for marking the pipeline. Marking have to be placed on every 50m along the pipeline, also on the places of horizontal break |  | 54 | kom
XIII | MARKING - TOTAL | Sub-total carried to Summary A.
A | SUMMARY A. - PIPELINE
Amount (euro)
I | PRELIMINARY WORK
II | EARTH WORK
III | FILLING
IV | CONCRETE WORK
V | REINFORCEMENT
VI | ASSEMBLY WORK
VII | PRESSURE TESTING
VIII | WASHING OUT AND DESINFECTION
IX | CROSSING WITH MAJOR ROAD
X | FITTINGS
XI | LOCKSMITH'S WORK
XII | WATERPROOFING
XIII | MARKING
A. | PIPELINE | TOTAL carried to Grand Summary - PART 3

## Bill No.12 MCB II - Cicevac
Bill No.12 - PIPELINE MCB II - CICEVAC
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
A | PIPELINE
I | EARTH WORK | B.2.
I.1 | Cleaning of the ground along the pipeline. Cleaning of the ground from bushes, verts, cutting stumps, removing mucks and waste. Accont by m² of cleared ground with running of material to the waste wich employer determine. 5247mX1,5m | B.2.1. | 7870.5 | m2
I.2. | Digging of the trench in the ground of II and III classification combined with 90% mechanic and 10% handy work for construction of the pipelines with even intercepion of edges of trench and displacement of the soil out of trench. On the places of the crossing with under-ground installation, digging must be handy.Acccount by m² of the excauation together with needed drawing water from the trench. | B.2.6. B.2.3. | 9656.7 | m³
I. 3 | Added excauation for the object on the pipeline routhe. Excaution of the soil II and III classification 80% mechanic and 20% handy work with postponement on temporary wate. The edges of excauation in the grade of 2:1 to the spot level of lower edge of the foudation plate. In the price, the drowing water is counted, drainage of undergraund water and atmospheric water also. | B.2.6. B.2.3.
I.3.1 | The manhole for VV (7 pcs) |  | 239.75 | m³
I.3.2 | The manhole for discharge VV (8 pcs) |  | 449.31 | m³
I.3.3 | The manhole for depletion |  | 52.99 | m³
I.3.4 | The manhole forsinking (3 pcs) |  | 579.24 | m³
I.3.5 | The manhole for of the flow meter |  | 72.52 | m³
I.4 | Planing of the bootom of the trench with know spot levels and with the falls eith the displacement of extra soil out of the trench. Acccount by m² of planing ground 5247x1.4. | B.2.5. | 7345.8 | m²
I.5 | After planing of the bootom of the trench it is needed to put send under the pipes for about 10cm and makes it plane, and around the waterpipes in the high of 70% of the gauge of the water pipes. | B.2.4. | 2840 | m³
I.6 | Covering of the trench on the routhe part out of roud with soil material from the excaution in the 20cm ply with needed compaction taking care not to damage joints and pipes. | B.3.1. | 3345.6 | m³
I.7 | Covering of the trench with grauel on the routhe part taking care of technical qualitificationsand plans. | B.2. | 30 | m³
I.8 | Filling and covering with materials around fodation plate and nanholes walls. Filling must be done in 30cm ply with wetting and compacting. | B.2.
I.8.1 | The manhole for VV (7 pcs) |  | 168.35 | m³
I.8.2 | The manhole for discharge VV (8 pcs) |  | 280.78 | m³
I.8.3 | The manhole for depletion |  | 33.64 | m³
I.8.4 | The manhole forsinking (3 pcs) |  | 297.54 | m³
I.8.5 | The manhole for of the flow meter |  | 51.15 | m³
I .9 | Covering spreading and sinking of grauel material under the foundation plate for about d=10 cm. Grauel used for covering shouldn't content organic and nonorganic materials, subject of decay and swelling. Account by m³ engaged grauel. | B.2.4.
I .9.1 | The manhole for VV (7 pcs) |  | 6.51 | m³
I .9.2 | The manhole for discharge VV (8 pcs) |  | 12.36 | m³
I .9.3 | The manhole for depletion |  | 1.44 | m³
I .9.4 | The manhole forsinking (3 pcs) |  | 12.6 | m³
I .9.5 | The manhole for of the flow meter |  | 1.35 | m³
I.10 | Running of extra material from the excauation to 3km, on location wich is determind by the supervisor, with loading, transport, unloading and crude planing of material on the wate. | B.2. | 6339.5 | m³
I | EARTH WORK - TOTAL | Sub-total carried to Summary A.
II | TRENCH PROTECTION
II.1. | Bracing of the trench sides support on the parts with depth over 1,3m along all depth and length. Bracing do together with progressions of the excaution with all regulations for this kind of work. Removing supoport do together with covering of trench taking care not to demage pipes, joints and objects. 2000x1,7x2 | B.7. | 6800 | m²
II | TRENCH PROTECTION - TOTAL | Sub-total carried to Summary A.
III | CONCRETE WORK | B.6.
III.1 | Mass concrete | B.6.
III.1.1 | Construction of layer ply for mass concrete manholes MB20, d=10 cm,over buffered ply of gravel. | B.6.
III.1.1.1 | The manhole for VV (7 pcs) |  | 6.51 | m³
III.1.1.2 | The manhole for discharge VV (8 pcs) |  | 12.36 | m³
III.1.1.3 | The manhole for depletion |  | 1.44 | m³
III.1.1.4 | The manhole for sinking (3 pcs) |  | 12.6 | m³
III.1.1.5 | The manhole for of the flow meter |  | 1.35 | m³
III.1.2 | Construction of anchor blocks from mass concrete MB 20 with details and technical conditions. | B.6. | 21.8 | m³
III.2 | Reinforced concrete | B.6.
It is alowed only constructions with mechanic-made concrete with characteristics claimed in statistic account, projescts, some positions of the bill of quantites.
Shutters won't be account separately, that value iz accounted in individual prices of the concrete works.
It is provided the use of the smooth shuttters if it is not different said in some positions of the bill of quntites.
Deviation from desingned plane, dimensions and heigh of the spot levels, musn't be over ±5 mm.
| Reinforced concrete as effluent head of the manhole for washing out. | B.6. | 1.4 | m³
III.3 | Concrete work of reinforced concrete manholes on the routhe of waterpipes do with concrete MB 30 with watertightness of V6 in the smooth shutters. Before concrete work, built in holes for passing pipes acording to plans of shutters. | B.6.
III.3.1 | The manhole for VV (7 pcs) |  | 28 | m³
III.3.2 | The manhole for discharge VV (8 pcs) |  | 59.96 | m³
III.3.3 | The manhole for depletion |  | 7.24 | m³
III.3.4 | The manhole for sinking (3 pcs) |  | 126 | m³
III.3.5 | The manhole for of the flow meter |  | 6.87 | m³
III.4 | Prefabricated upper slab - reinforced concrete MB30. | B.6.
III.4.1 | The manhole for VV (7 pcs) |  | 4.41 | m³
III.4.2 | The manhole for discharge VV (8 pcs) |  | 10.17 | m³
III.4.3 | The manhole for depletion |  | 1.17 | m³
III.4.4 | The manhole for sinking (3 pcs) |  | 16.2 | m³
III.4.5 | The manhole for of the flow meter |  | 1.05 | m³
III | CONCRETE WORK - TOTAL | Sub-total carried to Summary A.
IV | STEEL BENDING WORKS | B.8.
IV.1. | Suply, construction and bulit in of the refinforcing for the object on the pipline according to the techical conditations and plans RA 400/500 | B.8.
Account by kg of the evaluated amount of need refinforces.
IV.1.1 | The manhole for VV (7 pcs) |  | 2916.9 | kg
IV.1.2 | The manhole for discharge VV (8 pcs) |  | 6311.7 | kg
IV.1.3 | The manhole for depletion |  | 756.9 | kg
IV.1.4 | The manhole for sinking (3 pcs) |  | 12798 | kg
IV.1.5 | The manhole for of the flow meter |  | 712.8 | kg
IV | STEEL BENDING WORKS - TOTAL | Sub-total carried to Summary A.
V | ASSEMBLY WORK | B.3.
V.1 | Supply, transport, delivery along the trench and mounting of the pipes, together with couplings and all needed materials. | B.3.1.
| PE pipes DN 400 |  | 5458 | m'
V.2 | Fitting
V.2.1 | Butterfly valve on hand drive-butterfly vavle on handy driving PN 10. Incorporated measures are responded to standards:EN 593 ( JUS M.C5.005, DIN 3202). The flanges on the butterfly valve are in conpatibility with standard EN 1092 (JUS M.B6.011, DIN 2503). Valves are made of: • case - alloy steel cast SG GGG-40 • body of the seat - austenic black steel •disk - alloy steel cast SG GGG-40 • mandrel - chromed steel • blocking ring - EPDM • reductot case- steel cast GG 25 • AKZ protection - EKB epoxide coat of blue clour. Aslo deliver of the cementing materials (screws, nuts, shims) for the flange joints. | A.2.3.2.1.
| DN 350 PN 10 |  | 20 | pcs
V.2.2 | Butterfly valve on electric motor driveelekto motorni pogon - PN 10. Incorporrated measures are respondes to standards :EN 593 ( JUS M.C5.005, DIN 3202). The flanges on the butterfly valve are in conpatibility with standards EN 1092 (JUS M.B6.011, DIN 2503). Valves are made of: • case - alloy steel cast SG GGG-40 • body of the seat - austenic black steel •disk - alloy steel cast SG GGG-40 • mandrel - chromed steel • blocking ring - EPDM • reductot case- steel cast GG 25 • AKZ protection - EKB epoxide coat of blue clour. Auma electro driving defined in electro section | A.2.3.2.2.
| DN 350 PN 10 |  | 1 | pcs
V.2.3 | Flat valve - vavle with short body PN 10. Incorporrated measures are respondes to standards: EN 1171 (JUS M.C5.005, DIN 3202).Conecting mesaures of the flanges are in standards EN 1092 (JUS M.B6.011, DIN 2503). Case made of alloy steel cast spindel chromed steel, gasket of mandrel elastomer. Iner liner allowed for drinking water, outer protection with EKB expoxide coat of blue colur RAL 5015. Aslo deliver of the cementing materials (screws, nuts, shims) for the flange joints. | A.2.3.2.3.
V.2.3.1 | DN 200 PN 10 |  | 2 | pcs
V.2.3.2 | DN 100 PN 10 |  | 9 | pcs
V.2.3.3 | DN 50 PN 10 |  | 8 | pcs
V.2.4 | Air valve -intake air valve dimensions of the flanges and holes to EN 1092-2, PN 10; material body -a lloy steel cast, ball austentnic black steel. Deliver aslo the set of cementing materials (screws, nuts, shims) for the flange joints, according to the standards of productors. | A.2.3.2.5.
| DN 50 NP 10 |  | 8 | pcs
V.2.5 | Flow meter - Electromagnetic flow meter with the flanges, holes on the flanges PN 10. Deliver aslo the set of cementing materials (screws, nuts, shims) for the flange joints, (-BF1), with sensors installed on pipeline and long distance signal conlertor placed on the wall in the manhole, with local parametar (display unit), in the degree or prtection IP67, with analogy output 4-20mA, impulse output for cumulative flow and with the ability of signalization of the failure, as the type SITRANS F M MAGFLO MAG5000, or similar Voltage of power 230V AC. With flow meter special signal cables are delivered, withenought lenght, for conecting sensors of the flow and signals converctors. | A.2.3.2.6.
| DN 350 PN 10 |  | 1 | pcs
V.2.6 | Instalation dismantling pices PN 10. Incorprated measures are responded to JUS (DIN) standards.Conecting measures of the flanges are in compatibility with standards EN 1092 (JUS M.B6.011, DIN 2503). The flanges, set black flange and tigtening piece are nade of quality steel cast, range of the adjustnent of the length +/-25 mm. Aslo deliver of the jointing materials (screws, nuts, washers) for the flange joints.DN 100 PN 10 | A.2.3.2.4.
V.2.6.1 | DN 350 PN 10 |  | 20 | pcs
V.2.6.2 | DN 100 PN 10 |  | 9 | pcs
V.2.7 | Check valve on discharge of the pipeline DN 100 in the west Morava. Incorporated measures are rasponeded JUS (DIN) standards. Conecting measures of the flanges are in conpatibility with standards EN 1092 (JUS M.B6.011, DIN 2503). The flanges, set black flange and tigtening piece are nade of quality steel ca standardima Priključne mere prirubnica su u skladu sa standardom EN 1092 (JUS M.B6.011, DIN 2503). Aslo deliver of the cementing materials (screws, nuts, shims) for the flange joints.. | A.2.3.2.
| DN 100 PN 10 |  | 2 | pcs
V.2.8 | Different phase pices of duktil cast according to the specification | B.3.3. | 8060 | kg.
V.2.9 | Steel pipes DN 350 I DN 200 for instalation in the closing tank in Cicevac | B.3. | 300 | kg.
V.3 | testing of pipeline on preasure - Ø400 | B.3.1. B.5.1. | 5247 | m
V.4 | Desin fection and wahing out of the pipeline - Ø400 | B.5.3. | 5247 | m
V | ASSEMBLY WORK - TOTAL | Sub-total carried to Summary A.
VI | LOCKSMITH'S WORK
All elements, which are not casted, are done according, to the pattern of the metal work and with the details from the project.
VI.1 | Construction and installation of creepers Č 240/360 Ø26 |  | 350 | kg
VI.2 | Construction and montage canal covers Ø700 with the carrying capacity of 50 kN |  | 20 | pcs
VI.3 | Construction and montage canal covers Ø600 with the carrying capacity of 50kN |  | 6 | pcs
VI | LOCKSMITH'S WORK - TOTAL | Sub-total carried to Summary A.
VII | CROSSING ACROSS THE STREAM FLOW
VII.1 | Steel bearer for fixng the pipeline for bridges protection of the pipes with tervol d=10cm covering with aluminium | A.2.2. | 140 | m'
VII | CROSSING ACROSS THE STREAM FLOW - TOTAL | Sub-total carried to Summary A.
VIII | PIPELINE UNDER THE ROAD TRAFFIC
VIII.1 | Pipeline under the road traffic, railways installation of protective steel pipe | A.2.2.
| DN 600 d=10 |  | 76 | m'
VIII | PIPELINE UNDER THE ROAD TRAFFIC- TOTAL | Sub-total carried to Summary A.
IX | EMBEDDING OF THE PIPELINE
IX.1 | Embedding of the pipeline under the banks, major roads and railways | A.2.2. | 76 | m'
IX | EMBEDDING OF THE PIPELINE - TOTAL | Sub-total carried to Summary A.
X | THE OTHER WORKS
X.1 | Installation of the beacons - cast iron signs in the area of cross-roads on the places of horizontal break of the route. |  | 10 | pcs
X | THE OTHER WORKS - TOTAL | Sub-total carried to Summary A.
A. | SUMMARY A. - PIPELINE
Amount (euro)
I | EARTH WORK
II | TRENCH PROTECTION
III | CONCRETE WORK
IV | STEEL BENDING WORKS
V | ASSEMBLY WORK
VI | LOCKSMITH'S WORK
VII | CROSSING ACROSS THE STREAM FLOW
VIII | PIPELINE UNDER THE ROAD TRAFFIC
IX | EMBEDDING OF THE PIPELINE
X | THE OTHER WORKS
A. | PIPELINE TOTAL | TOTAL carried to Summary Bill No.12
B | METERING AND REGULATION MANHOLE "CICEVAC"
General Remarks
With this bill of quantities and priced billof quntites include delivery, montage, testing, realising to drive, probation and presentation of alal materials and equpment which are notified in some postions. Also, priceincludes delivery and installation of all small unspecified materials needed for the setting the equpement and works, aslo for the bringing up in the previous condition the parts of the other works dameged during installations fromthis project. Prices include construcations for all needed workshop documents needed for manufacturing, montage, testing,realising to drive and meintance of equipement.
All used material must be the first class quality and to respond to the standards. All works must be cary out with skilled workers and according to srbian tehnical regulations for this kind of work.
1. | DISTRIBUTION-CONTROL CUBICLE+1NG
1.1. | Distribution- control cubicle (+1NG) installated in mesauring - regulation manhole, made of two times pickled sheet, protected base and covering colurs and final plasticized, in the rate of mechanical protatin IP55, with doors on the front side. Cubicle is ment to be montaged on the wall, similar dimensions 600x700x350mm (ŠxVxD), and placed on the height ofi 0.9m from the spot level of the floor, with jalousies ( with filters) for ventilation on lower side of the door and on upper right part of the cubicle. Entrance for cables is on the upper side. On the right side of the cubicle 3 socket outlet is placed, in og preformance. It is requred to protect the posibility of locking distribution cubicle with typical key. The cubicle must be delivered complitely. finished, tested and ready for installation of cables. | C.1.3.
In the cubicle and on door of the cubicle are installated of following equipment:
| Main switch, with 2 positions 0-1, three pole, 25A, 400VAC, with 1NO i 1NC signal contact, installated on the cubicle door- 1 piece | C.1.3.
| Three- phase undervoltage realy(300-430V) for the control of voltage, order of phase and asymetry of phase - 1 piece | C.1.3.
| Automatic installational low voltage switch Ctype, with following features : Rated voltage : 440VAC Rated voltage : 6A Number of poles : 3 Rated sunspension power : 10kA - 1 piece | C.1.3.
| Automatic installational low voltage switch C type, with following features : Rated voltage : 440VAC Rated voltage : 16A Number of poles :3 Rated sunspension power : 10kA - 1 piece | C.1.3.
| Automatic installational low voltage switch C type, with following features : Rated voltage : 250VAC Rated voltage : 16A Number of poles : 1 Rated sunspension power : 10kA - 1 piece | C.1.3.
| Automatic installational low voltage switch C type, with following features : | C.1.3.
Rated voltage : 250VAC
Rated voltage : 10A
Number of poles : 1
Rated sunspension power : 10kA - 1 piece
| Automatic installational low voltage switch C type, with following features : Rated voltage : 250VAC Rated voltage : 6A Number of poles : 1 Rated sunspension power : 10kA - 4 piece | C.1.3.
| Automatic installational low voltage switch C type, with following features : Rated voltage : 250VAC Rated voltage : 2A Number of poles : 1 Rated sunspension power : 10kA - 3 piece | C.1.3.
| Automatic installational low voltage switch C type, with following features : Rated voltage : 250VAC Rated voltage : 10A Number of poles : 2 Rated sunspension power : 10kA - 1 piece | C.1.3.
| Automatic installational low voltage switch C type, with following features : Rated voltage : 250VAC Rated voltage : 4A Number of poles : 2 Rated sunspension power : 10kA - 2 piece | C.1.3.
| Automatic installational low voltage switch C type, with following features : Rated voltage : 250VAC Rated voltage : 2A Number of poles : 1 Rated sunspension power : 10kA - 2 piece | C.1.3.
| Automatic installational low voltage switch C type, with following features : Rated voltage : 24VDC Rated voltage : 2A Number of poles : 1 Rated sunspension power : 10kADC - 1 piece | C.1.3.
| Sign luminare, green, 230V AC with LED diode, for the montage on the cubicle door with board for signing for the presence of voltage - 3 pieces | C.1.3.
| Isolated transformer, 400/230V, 50Hz, rated power 400VA, as type ABL-6TS40U, - 1 piece | C.1.3.
| Three motor protective switch for the protection of the isolated transformer, 400/415V AC, 100kA, with cross current trigger (thermodynamics and electromagnet), rated current: (4-6.3)A, GV2-ME10 type, - 1 piece | C.1.3.
| Monophase transformer (-3T1) , 230VAC/24VAC, 50Hz, 300V, for connections of the socket outlet for low voltage - 1 piece | C.1.3.
| Stabilizational voltage unit, way in voltage 230V, 50Hz, wayout voltage 24VDC, 2A, with protection of the short joint, LED indicator of the function - 1 piece | C.1.3.
| Three pole motor - protective 690V, 10kA...100kA, with thermodynamic trigger for overloading protection and magnetic part fixed current of switching during short joints, with 2 pieces accessory contact singalization of the state 2NO with 1 piece of signal contact acting of protection, for type coordinations for motor power 1,5kW as type GV2 - PO8 | C.1.3.
| One pole three position choosed overlap, with "0" state (1-0-2), for drawing the way of work of Handy-Automatic gate, for installation on cubicle, 10A, 24VDC - 1 piece | C.1.3.
| Signal bulbs, fi 22mm, for installation on the cubicle door, 230V, 50Hz, with board, red colour - 1 piece | C.1.3.
| Signal bulbs, fi 22mm, for installation on the cubicle door, 230V, 50Hz, with board, green colour - 4 piece | C.1.3.
| Signal bulbs, fi 22mm, for installation on the cubicle door, 230V, 50Hz, with board, yellow colour - 1 piece | C.1.3.
| Push button with on still and one working contact, fi22mm, for installation on the cubicle door, 24V DC, with a board, red colour, as XB5 type - 1 piece | C.1.3.
| Push button with on still and one working contact, fi22mm, for installation on the cubicle door, 24V DC, with a board, green colour, as XB5 type - 2 piece | C.1.3.
| Push button with on still and one working contact, fi22mm, for installation on the cubicle door, 230V, 50Hz, with a board "test bulb", black coloured, as XB5 type- 1 piece | C.1.3.
| Diodes for testing bulbs - 6 pieces | C.1.3.
| Measuring apparatus milimetar indicator of cover opening, with 4-20mA way in with gauged scale from 0-100%, 72x72mm, for installation on the cubicle door - 1 piece | C.1.3.
| Accessory realy, for the coil voltage 230V, 50Hz, with a base, RC module for 230VAC and recovery bar, lap contact 6A 2 for installation on the rail- 4 pieces | C.1.3.
| Accessory realy, with a base for direct current, with 4 lap contact, with 24VDC winding type RXN-41G11BD+RXZ-7G+RXW040MD+RXZ-200+RXZ-300,- 5 pieces | C.1.3.
| Micro tracing logic routine (PLC), with compact processor unit (Compact CPU) with 14 digital ways in (voltage level 24V DC), 10 digital relay ways out, 2 analogy ways in and 1 analogy way out, integrated 2 RS 485 comunication interfaces (back up for PPI master and slave/MPI slave/Freeport protokol), : 140x80x62 mm (ŠxVxD), as type SIMATIC S7-200, CPU 224XP (AC/DC/Relay). Power supply voltage of controler 230V AC. - 1 set | C.1.4.
| Thermostat adjustment range 10...60°C, with one pair of way out contactsa 6A, 230VAC, 150mm, with a switch - 1 piece | C.1.3.
| Fluorescent lamp for ilumination internal door with fluo lamp 30W, 230V AC, length 150mm, with switch - 1 piece | C.1.3.
| Anticondensation heater 230 V, 50Hz, 30W - 1 piece | C.1.3.
| Microswitch for door 6A, 230VAC - 1 piece | C.1.3.
| Monophase outlet, 16A, 230VAC for installation on DIN rail way 2P+E - 1 piece | C.1.3.
| Monophase outlet for lower voltage, 10A, 24V AC, in OG for installation on the side of the cubicle door, 2P - 1 piece | C.1.3.
| Monophase outlet, 16A, 230VAC, in OG for installation on the side of the cubicle door - 1 piece | C.1.3.
| Threephase OG outlet , IP65, 16A, 400V, for installation on the side of the cubicle door - 1 piece | C.1.3.
| Different montage and bonding material, busbar, terminal, introduction cables, cords for wiring - 1 set | C.1.3.
1. | TOTAL - DISTRIBUTION CONTROL CUBICLE +1NG : 1 piece | Sub-total carried to Summary B.
2. | MEASURING - REGULATIONAL EQUPMENT IN THE MANHOLE
2.1 | Elektromotor drive regulation cover (+1UZ-Y01), located in measuring - regulation menhole, type AM3, with following features: | A.2.3.2.2.
multiturn actuators type SA
position duty with possibility of signalisation of immediate state (4-20mA)
with instalated contractors for both course of turning
power of electromotor 1.5kW; 2800min-1; 4A; 400V, 50Hz
with possibility of indication of extreme states covers and all signal break downs
| short time duty S2-15min. |  | 1 | pcs
2. | TOTAL MEASURING - REGULATION EQUPMENT IN THE MANHOLE: | Sub-total carried to Summary B.
3. | INSTALLATIONS IN THE MANHOLE
3.1. | Ending switch on the way in the object for signalisation need at the entrance to the manhole. | C.1.7. | 1 | pcs
3.2. | Basic earthing rod of the manhole of zinced lines FeZn 25x4mm JUS N.B4.901. The line is placed in the base of the object (manhole) and weld for the base armature on every 2m. Position creepers making connection with bus bar for equalization of the potential (SIP) | C.1.7. | 15 | m.
3.3. | Bus bar for equalization of the potential (SIP) made from copper railways 50x5mm. | C.1.7. | 1 | pcs
3.4. | Connection all metal mass (distributing-control cubicle, pipeline, metal ways in the manhole) on the bus bar for equlaization of potentional SIP cable PP-Y 1x25mm2 type and suitable coupling material. Total for work, material and transport. | C.1.7. | 1 | set
3.5. | Bridge of the valve and the flange (copper guilloche, clouts). | C.1.7. |  | sum
3.6. | Protective PVC pipes Fi 50mm, 1m, for introduction of voltage energetic cable in the manhole. Laying on the deepth of 0.7m | C.1.7. | 2 | pcs
3.7. | Finishing works for el. Installations in the manhole. After finishing work on carrying out of installations, contractor must: | C.1.7.
patch walls on where the installations pass
'remove technic and aesthetic errors of carrying out installations in the object (manhole)
'clean room from waste and take it out.
After finishing of summary of the work measure according to regulations and test
measuring resistance of isolating cables and electro equipment
measuring resistance of loop, testing conditions of electric striking protection
measuring of galuanic connections in instalations for equalization of potentional
measuring crossing voltage of earth works
| After measuring, contractor will make protocol and supply to the employer all needed certificate with authorized values |  | 1 | sum
3. | TOTAL INSTALLATIONS IN THE MANHOLE | Sub-total carried to Summary B.
4. | CABLE AND CABLE EQUIPMENT:
4.1. | Laying, settting out, and connecting on the both sides energetic and conduct-signal cables | C.1.6.
Cables are layed along cable wall-unit, down the walls and on the floor in protective metal pipes
4.1.1 | PP00-Y 4x2.5 mm2 | C.1.6. | 10 | m.
4.1.2 | PP00-Y 3x1.5 mm2 | C.1.6. | 10 | m.
4.1.3 | IY(St)Y 5x2x0.8 mm | C.1.6. | 10 | m.
4.1.4 | LiYCY 5x2x0.8 mm2 in plastic pipes | C.1.6. | 10 | m.
4.1.5 | LiYCY 2x0.75 mm2 in plastic pipes | C.1.6. | 20 | m.
4.2. | Idevlivery of materials and montage of preforated (PNK) cable bearer with all need equipment ( bearer, joint, screws) All together by the length meter. | C.1.6.
| - PNK 100 |  | 3 | m
4.3. | Resilent sapa pipes for protections of cales different dimensions | C.1.6. | 5 | m
4. | TOTAL CABLE AND CABLES EQUIPMENT: | Sub-total carried to Summary B.
5. | FINISHING WORKS
5.1. | Aplicative softer making ( programing of controler) |  | 1 | set
5.2. | Testing and dedication PLC |  | 1 | set
5.3. | As built documentation |  | 1 | set
5. | TOTAL FINISHING WORKS | Sub-total carried to Summary B.
B. | SUMMARY B. - METERING AND REGULATION MANHOLE "CICEVAC"
Amount (euro)
1 | DISTRIBUTION-CONTROL CUBICLE+1NG
2 | MEASURING - REGULATIONAL EQUIPMENT IN THE MANHOLE
3 | INSTALLATIONS IN THE MANHOLE
4 | CABLE AND CABLE EQUIPMENT:
5 | FINISHING WORKS
B. | METERING AND REGULATION MANHOLE "CICEVAC" - TOTAL | TOTAL carried to Summary Bill No.12
C | CROSSING UNDER THE WEST MORAVA RIVER
I | EARTH WORKS
I.1 | Works in the river channel carry out in the low water, when the flow is minimal(fall). Flow of water deviate in one side of the channel, and carry out work on the other side with pumping out underground water. First, place concrete protective pipe Ǿ700 ,length 1-2 m on depth about 1m of the river botttom. After finishing work on one side, do the same on the other side. After that, from the manhole from one side of the river sink steel pipeline Ǿ 400 with responding dolly. Steel pipeline must be maximum protected out and in. Excavation in gravel material for placing the pipeline 92m x 1,3m x 1,20m. | B.2. | 143.52 | m3
I.2 | Excavation for deviation of river flow | B.2. | 500 | m3
I.3 | Ground excavation for producing RC manholes of watertightness concrete dimension 4mx2mx5m and 2mx2mx5m in IV class ground. | B.2. | 100 | m3
I | EARTH WORKS - TOTAL | Sub-total carried to Summary C
II | TRENCH PROTECTION
II.1. | Bracing of of the manhole trench support do on the part with depth more than 1,3 m.Bracing must be done both with excavation, and under the terms for this kind of work. Support removal must be done with finishing of work. | B.7. | 92 | m²
II.2. | Taking out surplus material from the excavation to 3 km, on location which supervisor determine, with loading, transport, unloading and crude planning of material on the waste. | B.4. | 80 | m3
II | TRENCH PROTECTION - TOTAL | Sub-total carried to Summary C
III | CONCRETE WORKS | B.6.
III.1 | Unreinforced concrete: producing state ply for unreinforced manholes MB20, d=10 cm, over recorded tampon ply of gravel | B.6.
III.1.1 | Manhole |  | 1.2 | m³
III.1.2 | Manhole |  | 0.8 | m³
III.2 | Reinforced concrete: Installation watertightness reinforced concrete MB30 with shutters and reinforcing. Walls are o,3m. Shutters will not be account separately, that value is in separately prices of concrete works. Use of flat shutters is considered. | B.6.
III.2.1 | Manhole 1 |  | 25 | m³
III.2.2 | Manhole 2 |  | 18 | m³
III | CONCRETE WORKS - TOTAL | Sub-total carried to Summary C
IV | STEEL BENDING WORKS | B.8.
IV.1. | Supply, construction and installation of reinforcing for pipeline objects according to technical conditions and plans RA 400/500 . Account by kg of accessement quantity of reinforcing. | B.8.
IV.1.1 | Manhole 1 |  | 2250 | kg
IV.1.1 | Manhole 2 |  | 1620 | kg
IV | STEEL BENDING WORKS - TOTAL | Sub-total carried to Summary C
V | ASSEMBLY WORK
V.1 | Supply, transport and montage of concrete pipe, both with joint and all needed materials. | B.3.
V.1.1 | Concrete pipe DN 700 |  | 92 | m'
V.1.2 | Steel pipe DN 400 |  | 92 | m'
V.2 | Butterfly valve on handy drive. Supply, delivery and montage of butterfly valves on handy drive PN 10. Engaged measures standardsEN 593 ( JUS M.C5.005, DIN 3202) EN 1092 (JUS M.B6.011, DIN 2503). Valves are made of: •case- alloy steel cast SG GGG-40 •body of the seat - austentic black steel • disk - alloy steel cast SG GGG-40 • osovinamandrel - chromed steel • blocking ring - EPDM • reductor case - alloy steel GG 25 • AKZ protection - EKB epoxide coating of blue colour Also deliver a set of cementing materials (screw, nuts) for flange joints. | A.2.3.2.1.
V.2.1 | DN 400 PN 10 |  | 2 | pcs
V.2.2 | DN 100 PN 10 |  | 1 | pcs
V.3 | Instalation dismantling pices PN 10. Incorprated measures are responded to JUS (DIN) standards.Conecting measures of the flanges are in compatibility with standards EN 1092 (JUS M.B6.011, DIN 2503). The flanges, set black flange and tigtening piece are nade of quality steel cast, range of the adjustnent of the length +/-25 mm. Aslo deliver of the jointing materials (screws, nuts, washers) for the flange joints. | A.2.3.2.1.
V.3.1 | DN 400 PN 10 |  | 2 | pcs
V.3.2 | DN 100 PN 10 |  | 1 | pcs
V.4 | Check valve - supply, delivery and istallation Check valve on discharge of pipeline DN 100in in South Morava. Recorded mesaures are according to JUS (DIN) standards. Connecting meansure of the flage in standard EN 1092 (JUS M.B6.011, DIN 2503). Deliver also the set of cementing materials (screw, nuts ) for flange joints. | A.2.3.2.
V.4.1 | DN 100 PN 10 |  | 1 | pcs
V.4.2 | Different fittings of ductil cast according the specification | B.3.3. | 976 | kg.
V | ASSEMBLY WORK - TOTAL | Sub-total carried to Summary C
VI | LOCKSMITH'S WORK
VI.1 | All not castings elements has to be produced in accordance to dwgs and details from the project
VI.1.1 | Making and building into ladders St240/360 Ø26 |  | 32 | pcs
VI.1.2 | Making and assemblies shaft lids Ø700 nosivosti 50kN |  | 2 | pcs
VI | LOCKSMITH'S WORK - TOTAL | Sub-total carried to Summary C
VII | EMBEDDING OF THE PIPELINE
VII.1 | Embedding of pipeline DN 400 after placing concrete pipe DN700 | B.3. | 92 | m'
VII | EMBEDDING OF THE PIPELINE - TOTAL | Sub-total carried to Summary C
C | SUMMARY C - CROSSING UNDER THE WEST MORAVA RIVER
Amount (euro)
I | EARTH WORKS
II | TRENCH PROTECTION
III | CONCRETE WORKS
IV | STEEL BENDING WORKS
V | ASSEMBLY WORK
VI | LOCKSMITH'S WORK
VII | EMBEDDING OF THE PIPELINE
C. | CROSSING UNDER THE WEST MORAVA RIVER - TOTAL |  | TOTAL carried to Summary Bill No.12
| SUMMARY Bill No.12 |  |  |  |  | Amount (euro)
A. | PIPELINE
B. | METERING AND REGULATION MANHOLE "CICEVAC"
C. | CROSSING UNDER THE WEST MORAVA RIVER
Bill No. 12 | PIPELINE MRB II - CICEVAC | TOTAL carried to Grand Summary - PART 3
Note on B145: ZOSIMI: Provjeriti dali je prikazano u IWA Projektu!?

## Bill No.13 WT Varvarin
Bill No.13 - WATER TANK VARVARIN
Item No. | Description | Specification Clause | Quantity | Unit | Rate (euro) | Amount (euro)
A | RESERVIOR
I | PRELIMINARY WORKS | B.1.
I.1 | Geodetic works needed for setting up the site with making objects, site survey construction | B.1.3. | 1 | sum
I | PRELIMINARY WORKS -TOTAL | Sub-total carried to Summary A.
II | EARTH WORKS | B.2.
II.1. | Cutting trees with motor saw with trimming of branches and putting then on the side | B.2.1.
II.1.1. | Spongy wood F 10-20 cm | B.2.1. | 5 | pcs
II.1.2. | Spongy wood F 20-30 cm | B.2.1. | 5 | pcs
II2.2. | Handy clearing of bushes with transporting to max. 20 m. | B.2.1. | 2583 | m2
II.3. | Machine excaution of ground with a dredger | B.2.6.
| Excaution of 3 class ground with deep bucket with capacity of 950l. | B.2.6. | 4220 | m3
II.4. | Handy excautation of the ground for objects foundation or cannal trench latitude 1-2 m. Digging has to be done with one of the tool with accuracy of ±5m. Dig ground put from the edge on length of 1,0m. Digging has to be handy with shovels from a support to a support. It is normed also work braces and replacing of dig materials. | B.2.2.
| Digging in 3 class ground naturaly wet depth 2-4 m. | B.2.3.2. | 405 | m3
II.5. | Planing of ground on mitre surface of 3 class ground, with accracy of ±3 cm, with medium excavation of 0,05 m3/m2 and transport of material to 50m. | B.2.5.1. | 1250 | m2
II.6. | Supply, delivery and installation of broken stone for construction tampon ply under the tank. In prise is accounted replacing with sinking with handy compaction hammer of 10 kg, by needed degree of density.. | B.2.4. | 225 | m3
II.7. | Filling and covering without thumping it is normed replacing transported materials to 3,0 m. Transpot of material for more than 3,0 m is not normed it's paid by GN-900 | B.2.4.4. | 4625 | m3
II.8. | Machine excavation of top soilwith soil transport to 20 m max. | B.2.6. | 260 | m3
II.9. | Broken stone supplay, handy replacing and construction of broken stone broad surface in ply of 10 cm by rolling, for access road. | B.2.4. | 154 | m2
II.10. | Compression of tampon ply and covering trenches with vibro plates of moduls Me=500 MP/cm2. Play depth is 40 cm, and machine is moving 1km/h. | B.2.4.5. | 1105 | m2
II.11. | Handy local transport | B.4.1. | 4625 | m3
II | EARTH WORKS - TOTAL | Sub-total carried to Summary A.
III | CARPENTRY WORKS | B.7.
III.1. | Foundation shutters, machine funndament and flat concrete walls off 24 mm - boards-two sides shuters . It's normed transport of shutters to the installlation place. | B.7.
III.1.1. | Shutter erection of foundation plate. | B.7. | 55.92 | m2
III.1.2. | Shuttter erection outer walls of the tank. | B.7. | 1215 | m2
III.1.3. | Shuttter erection walls between water chamber of the tank. | B.7. | 405 | m2
III.1.4. | Shutter erection walls of tank gates. | B.7. | 337.44 | m2
III.2. | Flat palte shutter with vuts with supporting with wooden supporters to 3,0 m. It's normed transporter of shutters to the installation place, transport from floor to floor transport to wate to 30 m. | B.7.
| Shutter erection of upper plate of the tank. |  | 1012.5 | m2
III.3. | Flat plate shutter no matter of the surface with supporting wood support to the support lenght of 3,0 m. It is normed transport to the installation place from floor to floor, and material transport to the waste to 30 m. | B.7.
| Shutter erection of the gate plate | B.7. | 44.32 | m2
III.4. | Flate gradual point shutter it is normed transport to the instalation place, from floor to floor, and material transport to the waste to 30 m. | B.7.
| Stairways shutter in the gate. | B.7. | 5.84 | m2
III.5. | Flat beam shutter, foting frames and stauncheons - without tines, from 24 mm boards. It is normed transport to the installation place from floor to floor, and material transport to the waste to 30 m. | B.7.
| Stauncheon shutter in water chambers. | B.7. | 185.8 | m2
| Pipeline support in the gate | B.7. | 4.8 | m2
III | CARPENTRY WORKS - TOTAL | Sub-total carried to Summary A.
IV | STEEL BENDING WORKS | B.8.
IV.1. | Supply and handy cutting correcting, fleixing installating and bonding simple and complex rainforcing. It is normed: correction with handy bond, cutting with mobile and stable scissors claring from dirt, fat and pelling rust handy flaxing on rainforcing table and grading with ditailes marking inastalling and bonding according to the plan, local transport also: handy transport of reinforcing to the site on 20 m to scip lifting to 15 m with "scip" lift and handy transport to 20m per object. | B.8.
IV.1.1. | F 4 - 12 mm | B.8. | 33405 | kg
IV.1.2. | F 14 and more mm | B.8. | 35868 | kg
IV.2. | Supply and installation reinforcing of NET of CMB for reinforcing walls F 6,5-8mm.
| F 6,5-8 mm | B.8. | 3462 | kg
IV | STEEL BENDING WORKS - TOTAL | Sub-total carried to Summary A.
V | CONCRETE WORK | B.6.
V.1. | Supply handy installation of concrete construction of little section of 0,12 m3 to 0,30 m3 concrete on m2 or m1 concruction is suitable to level spot 0,00 lower. For unreiforced concruction - wet concrete is normed: wetting of the shutters, putting in concretein the shutters or excavation distribution of concrete in ply, sinking concrete with wooden tool and knocking in the shutters, flating of ground, replacing funnels and paltforms, placing and replacing fosna concrete transport. For reinforced concructions plastic concrete is normed: wetting excavation putting in concrete in the shutters or excavation distribution of concrete in ply sinking concrete with wooden tools and knocking in the shutters, placing and replacing for concrete transport, also segregation reinforcing from the shutters if it moved. Reinforcing must be covered with protective concrete ply and must stay on it is place. Transport of unreinforced and reinforced concrete needs operations as: concrete loading in japaner from the storage bim transport to 20m from the object, unloading on the platform. | B.6.
V.1.1. | Unreinforced constructions - wet concrete MB15 - tampon ply under the tank | B.6. | 168 | m3
V.1.2. | Unreinforced constructions - wet concrete MB20 - producing support of pipeline in the gate in the tanks | B.6. | 63.6 | m3
V.1.3. | Reinforced constructions - plastic concrete MB30 producing walls of the tank | B.6. | 287.2 | m3
V.1.4. | Reinforced constructions - plastic concrete MB30 producing walls of the gate | B.6. | 30.5 | m3
V.1.5. | Reinforced constructions - plastic concrete MB30 producing walls in the tank | B.6. | 90 | m3
V.1.6. | Reinforced constructions - plastic concrete MB30 producing lower plate of the tank | B.6. | 336.5 | m3
V.1.7. | Reinforced constructions - plastic concrete MB30 producing lower plate of the gate | B.6. | 6.2 | m3
V.1.8. | Reinforced constructions - plastic concrete MB30 producing upper plate of the gate | B.6. | 271.3 | m3
V.1.9. | Reinforced constructions - plastic concrete MB30 producing upper plate of the gate with acornice | B.6. | 4.8 | m3
V.1.10. | Reinforced constructions - plastic concrete MB30 producing plate with griders | B.6. | 3.6 | m3
V.1.11. | Reinforced concructions - plastic concrete MB30 producing plate with griders | B.6. | 1.5 | m3
V.1.12. | Unreinforced constructions - wet concrete MB15 ply with flow on the upper side of the tank | B.6. | 100 | m3
V | CONCRETE WORK - TOTAL | Sub-total carried to Summary A.
VI | MASONRY WORK | B.9.
VI.1. | Construction brick wall d=12 cm in extensional mortar 1:3:9. Making mortar is accounted, in the price, also handy transport of bricks and mortar and bricking | B.9.2. | 83.5 | m3
VI.2. | Installation different small things. It is normed: all material transport is on 20m horizontal, 15 m upright and carrying mortar with abucked to the place of installation to 10m. Making must be with a mixer. | B.9.
VI.2.1. | Placing and installations crampons which is instalated in the shutters | B.9. | 22 | pcs
VI.2.2. | Placing and installations ventilation head. | B.9. | 8 | pcs
VI.3. | Laying and installation of the cover frame. It is normed transport of the cover and mortar to 20m japoner and carying handy to 10m | B.9.
VI.3.1. | Laying and installation concrete and iron frames for the cover to 30kg | B.9. | 2 | pcs
VI.4. | Installation of doors to 2 m2 in concrete walls | B.9. | 1 | pcs
VI.5. | Installation of windows to 2 m2 in concrete walls | B.9. | 3 | pcs
VI.6. | Laying and installation cover frame made of deformed shed metal with locking lock, according to given details. | B.9. | 1 | pcs
VI | MASONRY WORK - TOTAL | Sub-total carried to Summary A.
VII | LOCKSMITH'S WORK
VII.1. | Construction and delivery of metal doors mason dimensions 100/200 cm, with ventional holes. |  | 1 | pcs
VII.2. | Construction and fixed Venetian shutters with protective net, dimension 90/50cm placed in doors. |  | 1 | pcs
VII.3. | Construction and installation of metal window dimensions 100x120cm. The window is glazed with glasses d=4mm construction of the window is according to the pattern and details of the productor |  | 1 | pcs
VII.4. | Construction and installation of metal window of structural steel and closed with pickled sheed. The window has a frame which is installated in the hole and wind of the window. Dimensions of the window are 100x100cm. The window also has needed window furniture. Window must be done according to the pattern and detailes of the productor |  | 2 | pcs
VII.5. | Construction and installation of metal cover made of 'L' structural steel and deformed sheed metal. The cover is for construction hole 100x145cm. Construction of the cover is according to the pattern and detailes of the productors |  | 1 | pcs
VII.6. | Construction of the metal protective fence made of steel boxy structual 40x40x30 and 30x30x3. Montage the fence on the side of the stairways and fence bonding do with RB12 steel shields. Construction of the fence is according to the pattern and detailes of the producers |  | 8 | m'
VII.7. | Supply delivery and installation of the wire net with a square mesh, from wire F2,5mm, height for fence construction. |  | 240 | m'
VII.8. | Construction and installation of entrance door, latitude 3m, made of pipes F5/4" and wire net. In the price is accounted needed hinges and a lock with a padlock |  | 1 | pcs
VII.9. | Supply delivery metal stauncheuns of height 3,0m made of black pipes F2" |  | 80 | pcs
VII | LOCKSMITH'S WORK - TOTAL | Sub-total carried to Summary A.
VIII | ASSEMBLY WORK | B.3.
VIII.1. | Supply and delivery casted iron phase pieces. | B.3.3. | 9325 | kg
VIII.2. | Supply and delivery following water pipe reinforcing, named pressure of 10,0 bars | B.3.4.
VIII.2.1. | Butterfly valve with the flanges and handy drive reductor - DN 150 | B.3.4. | 2 | pcs
VIII.2.2. | Butterfly valve with the flanges and handy drive reductor - DN 300 | B.3.4. | 4 | pcs
VIII.2.3.. | Butterfly valve with the flanges and handy drive reductor - DN 400 | B.3.4. | 2 | pcs
VIII.2.4. | Butterfly valve with the flanges and cheeck wight DN 300 | B.3.4. | 2 | pcs
VIII.2.5. | Regulation valve with water level in the tank with the flanges and ball float D300 | B.3.4. | 2 | pcs
VIII.2.6. | Armas ALFA-PE joint DN 300 | B.3.4. | 2 | pcs
VIII.2.7. | Air bag DN 400 | B.3.4. | 2 | pcs
VIII.2.8. | Frog cover DN 300 | B.3.4. | 1 | pcs
VIII.3. | Supply and delivery ventilatonal pipe with a cap and brass net for checking the enter of small animals to the tank. | B.3.4. | 8 | pcs
VIII.4. | Supply and delivery of gasket for flange joints. | B.3.
VIII.4.1. | DN 150 | B.3. | 58 | pcs
VIII.4.2. | DN 300 | B.3. | 48 | pcs
VIII.4.3. | DN 400 | B.3. | 22 | pcs
VIII.5. | Supply and delivery of screw with nuts and support for reinforcing joints and phase pieces | B.3.
VIII.5.1. | M20/75 mm | B.3. | 460 | pcs
VIII.5.2. | M20/90 mm | B.3. | 576 | pcs
VIII.5.3. | M24/100 mm | B.3. | 352 | pcs
VIII.6. | Installing and bonding on phase pices flanges and rainforcing. | B.3.
VIII.6.1. | DN 150. | B.3. | 62 | pcs
VIII.6.2. | DN 300 | B.3. | 44 | pcs
VIII.6.3. | DN 400 | B.3. | 19 | pcs
VIII.7. | Supply of cast- iron covers F625 mm JUS M.JG223 (carrrying 15 kM-with pane) |  | 2 | pcs
VIII.8. | Supply and transport Lg greepers for the menhole. |  | 22 | pcs
VIII.9. | Supply and installation dreinage PVC pipes in the tranches
| DN 160 | B.3. | 146 | m'
VIII.10. | Supply,transport and installation one -way lift one handy drive. It is positioned also"cad" hand drive and chain for propel of the ''cat''. |  | 1 | pcs
VIII.11. | Supply,transport and installation steel 124 bearer for carrying the lift. |  | 3.7 | m'
VIII.12. | Construction and installation steel plates, dimension 300x300x15mm, on which are casted ancer discharges from deformed steel bar F25. |  | 2 | pcs
VIII.13. | Supply and transport and installation steel flange DN150 PN10 | B.3. | 8 | pcs
VIII | ASSEMBLY WORK - TOTAL | Sub-total carried to Summary A.
IX | PAINTING WORK | B.10.
IX.1. | Oil paint painting of steel things. Account of plates and change of norm according to technical conditons. | B.10.4.
IX.1.1. | Painting of steel windows, doors and covers. | B.10.4. | 14 | m2
IX.1.2. | Pipe painting | B.10.4. | 74.56 | m2
IX.1.3. | Fence painting | B.10.4. | 8 | m2
IX | PAINTING WORK - TOTAL | Sub-total carried to Summary A.
X | WATERPROOFING
X.1. | Supply and delivery and instalation of waterproofing in 3 plies d=4 mm, with joint cast. In the price all work and material is accounted. |  | 3238 | m2
X.2. | 3 plies coating of walls and bottoms of the chambers with penetrate. |  | 1822.5 | m2
X.3. | Cleading colour coating on places whitch are not covered with ground. |  | 49.5 | m2
X | WATERPROOFING - TOTAL | Sub-total carried to Summary A.
XI | THE OTHER WORKS
XI.1. | Geodetic survey of a new built objects and analysis cadaster. | B.5.4. | 1 | sum
XI.2. | Washing out water chambers of the tanks and pipes after finishing off work | B.5.3.1. | 1 | sum
XI.3. | Desinfection a new built pipeline and water chambers of tanks. | B.5.3.2. | 1 | sum
XI | THE OTHER WORKS - TOTAL | Sub-total carried to Summary A.
XII | SHEET METAL WORK
XII.1. | Lining of cornice with galuanized sheet streching latitude 20 cm |  | 15 | m'
XII.2. | Lining of soil banks with galvanized sheet streching latitude 20 cm |  | 1 | m'
XII | SHEET METAL WORKS - TOTAL | Sub-total carried to Summary A.
A. | SUMMARY A. - RESERVOIR "VARVARIN"
Amount (euro)
I | PRELIMINARY WORKS
II | EARTH WORKS
III | CARPENTRY WORKS
IV | STEEL BENDING WORKS
V | CONCRETE WORK
VI | MASONRY WORK
VII | LOCKSMITH'S WORK
VIII | ASSEMBLY WORK
IX | PAINTING WORK
X | WATERPROOFING
XI | THE OTHER WORKS
XII | SHEET METAL WORK
A. | RESERVOIR "VARVARIN" | TOTAL carried to Grand Summary - PART 3

## Summary
GRAND SUMMARY
“Rasina District: Regional Water Supply Project” | Totals (€)
Bill No.1 - General items
PART 1 - WTP Majdevo
Bill No.2 - EQUIPMENT AND BUILDING WORKS FOR TECHNOLOGICAL PART
Bill No.3 - OZONE BLOCK
Bill No.4 - FLOCCULATION AND LAMELLAR SEDIMANTATION TANK
Bill No.5 - SAND FILTERS
Bill No.6 - UV DISINFECTION
Bill No.7 - BUILDING WORKS - ADMINISTRATIVE BUILDING
Bill No.8 - ELECTRICAL PART AND CONTROL
PART 2 - CCMS
Bill No.9 - CCMS FOR THE REGIONAL WATER SUPPLY SYSTEM CELIJE
Bill No.10 - MCB CICEVAC, VARVARIN, STALAC
PART 3 - Finalisation of transmission mains towards Cicevac and Varvarin
Bill No.11 - PIPELINE: MCB I - WATER TANK VARVARIN
Bill No.12 - PIPELINE MCB II - CICEVAC
Bill No.13 - WATER TANK VARVARIN
Sub-total No.1
Discount (if any)
Sub-total No.2
Contingencies 10 %
TOTAL OF TENDER (forward to Tender Form)

## Dayworks
SCHEDULE OF DAYWORK RATES
Item No. | Description | Unit | Rate (euro)
1. | Labour
The rates inserted below against each category of labour shall apply to hours worked by workmen only and shall include for all supervision by gangers and foremen. These rates shall include for overtime entitlements irrespective of the actual hours worked in each category. Allow for all costs in connection with mobilisation, provision and maintenance of equipment, permits, temporary measures, access roads, services etc. necessary for the execution of the works
1.1 | General labourer | hr
1.2 | Pipelayer | hr
1.3 | Machine driver | hr
1.4 | Steel fixer | hr
1.5 | M&E equipment erector/installer | hr
1.6 | Electrician | hr
1.7 | Carpenter | hr
1.8 | Mason/bricklayer | hr
1.9 | Welder | hr
1.10 | Transport driver | hr
2. | Materials
2.1 | Supply of materials not listed in Bills of Quantities and materials used for work carried out on a daywork basis shall be paid upon production of the invoice. The percentage added to the cost of material is to include for all handling and storage. 'The cost of materials means the actual price paid by the Contractor, net of all trade and other discounts rebates and allowances obtainable by the Contractor. The Contractor shall enter the % adjustment to the cost of materials delivered to site for profit and all overheads. | %
3. | Equipment
The quoted price shall include for provision, maintenance, fuel and lubricants, tools transport, attendance and driver/operator
3.1 | Pick-up 0.75 t | hr
3.2 | Compressor 4 to 6 cu.m/hr | hr
3.3 | Jack hammer | hr
3.4 | Generator 15 / 20 KVA | hr
3.5 | Plate vibrator | hr
3.6 | Tandem vibro roller 1 to. | hr
3.7 | Portable welding set | hr
3.8 | Dewatering pump 30 m³/hr | hr
3.9 | Tipper truck 7 to. | hr
3.10 | Tipper truck 10 m³ | hr
3.11 | Excavator 0,6 m³ | hr
3.12 | Front end loader | hr
3.13 | Bulldozer 70 - 100 kW | hr
3.14 | Poker vibrator | hr
3.15 | 100/150mm slurry pump | hr
3.16 | Concrete pump 20 m3/h | hr
3.17 | Dumper 1 cu.m | hr
3.18 | Trunk 30 to. | hr